## COVER
SUFA PROJECT
Yahchouch Mixed Intermediate Secondary Public School
"REEE" MEASURES
Bill Of Quantities
Client:

## Execution BoQ
BoQ for Execution
ITEM | DESCRIPTION | Quantities in TD | UNIT | Estimated Unit Price ($) | Total Price ($)
HYBRID SOLAR PV SYSTEM WITH STORAGE
INSTALLATION OF ITEMS:
1 | Monocrystalline Solar panels - 410Wp | 30 | Item
2 | Monocrystalline Solar panels - Spare Parts | 4 | Item
3 | Battery Bank (24 Batteries) including Steel Rack | 1 | Item
4 | DC Surge Protection Device : SPD DC (Onesto BY7-40/3-1000) | 2 | Item
5 | AC Surge Protection Device : SPD AC (Onesto BY7-40/4-385). | 2 | Item
6 | PV Cables: 1Cx4mm2 Annealed Tinned Flexible copper conductor solar DC cable (UV Protected, XLPO Insulated) | 150 | m
7 | MC4 Connectors | 12 | Pairs
PROCUREMENT & INSTALLATION OF ITEMS - TO BE AS PER THE DESIGN & SPECS OF THE RFP
8 | Three Phase Hybrid Inverter 12 kVA | 1 | Item
9 | DC disconnect switch - 20A | 2 | Item
10 | 2P DC fuses with fuse holder- 20A | 2 | Item
11 | DC cable - 70mm2 | TBD | m
12 | 2P DC Breaker - 200A | 1 | Item
13 | 2P DC Fuse with fuse holder - 200A | 1 | Item
14 | AC cable - 2x4mm2 | TBD | m
15 | AC cable - 4x10mm2 | TBD | m
16 | Earthing cable G/Y PVC insulated for equipment and steel structure grounding - 4mm2 | TBD | m
17 | Earthing cable G/Y PVC insulated for equipment and steel structure grounding - 16mm2 | TBD | m
18 | 4P AC breakers - 32A | 3 | Item
19 | 4P RCBO 300mA - 32A | 1 | Item
20 | 4P 63A AC Change over switches | 1 | Item
21 | - Power Meter on the AC output side as per the SLD - Phase Failure/ Over_Under voltage protection relay with corresponding Contactor on the AC input side as per the SLD | LS | Item
22 | Supply and Install all related componenents to ensure the porper load segragation including but not limited to (Cables, MTS, Breakers, Relays, Contatcors, Fuses,...) | LS | Item
23 | DC electrical panelboard, AC electrical Panelboards; to include all components of the SLD | LS | Item
LIGHTING
INSTALLATION OF ITEMS:
24 | Dismantling and Replacement of existing Fluorescent lighting including all required accessories and wiring. - T8 Bulbs, 120cm, 36W to be replaced with LED T8 Bulbs, 120cm, 18W. | 120 | Item
INDOOR AIR QUALITY SENSORS
INSTALLATION OF ITEMS:
IS sensors shall be connected to the nearby power plug; IS sensors shall be configured thru existing Wi-Fi access point (provided by the School IT Department).
25 | Installation, setup and configuration of Air Quality sensors as indicated in the Drawings. | 8 | Item
GENERAL ITEMS
26 | Testing and commissioning of all Electrical Systems, including training the School staff to handle the systems. | 1 | Item
27 | Identification and labeling of cables, wires, panel boards and all other equipment mentioned in this BOQ . | 1 | Item
28 | Net metering application and installation | 1 | Item
29 | Safety equipment: One fire extinguisher & one Hydro Fluoride sensor with alarm | LS | Item
30 | Steel structure for PV panels, including all necessary accessories | LS | Item
31 | Transportation of energy items from LCEC warehouse to the school | LS | Item
32 | New earthing system dedicated to the PV system | LS | Item
33 | Energy Study for ZG - Energy production simulation and savings estimation | 1 | Item
34 | Material Submittals, Shop drawing and As-Built drawings, Operation and Maintenance Manuals | 1 | Item
OPTIONAL ITEM (MIGHT NOT BE INCLUDED - TO BE PRICED)
35 | External Lighting Protection System (LPS) | LS | Item
Total