SECTION 220513 - Common Motor Requirements for Plumbing Equipment

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Single phase electric motors.

          - Three phase electric motors.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 22 Sections specifying plumbing assemblies motorized components.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings.

        - AFBMA 11 - Load Ratings and Fatigue Life for Roller Bearings.

        - IEEE 112 - Test Procedure for Polyphase Induction Motors and Generators.

        - NEMA MG 1 - Motors and Generators.

        - NFPA 70 - National Electrical Code.

        - Conform to all AFBMA, IEEE, NEMA, NFPA, and California Title 24 standards, codes, and regulations.

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing - Review of Materials" and Division 01 Section "General Requirements."

        - Pre-Construction Submittals:

          - Submit for all equipment prior to ordering or fabrication.  No deviations from the submittals as approved shall be permitted and materials purchased prior to approval shall be at the sole risk of the Subcontractor.

          - All submittal data shall be the same size for group of information and shall be bound or in a three-ring binder as appropriate.  All information shall be indexed and tabbed with reference to the specific section of the specification.

          - Product Data:  Provide wiring diagrams with electrical characteristics and connection requirements.

          - Manufacturer's Installation Instructions:  Indicate setting, mechanical connections, lubrication, and wiring instructions.

          - Field reports:  Submit hand-written or printed reports indicating operating conditions after detailed check out of systems prior to construction.

        - Project Record Documents:

          - Submit under provisions of Division 01 Section "General Requirements.".

          - The construction subcontract drawings shall be submitted in "red-line" marked-up form which the University will use to produce the "as-builts".

          - Additional shop drawings produced by the subcontractor shall be revised to show the "as-built" conditions prior to submittal.  Submit as-built shop drawings and copies of all computer files developed for this subcontract.

          - Equipment locations:  Show actual locations of all system components and affected equipment including motors, driven equipment, and electrical panels.

          - Mounting details:  Accurately record mounting details.

          - Motor Schedule:  Provide an update which includes all connected motors installed.

        - Operating And Maintenance Data:

          - Submit under provisions of Division 01 Section "Special Procedures".

          - Operation Data:  Include instructions for safe operating procedures.

          - Maintenance Data:  Documentation shall include manufacturers model number, manufacturer's installation instructions, assembly drawings, bearing data including replacement sizes, lubrication instructions, adjustment procedures, inspection period, recommended cleaning methods and materials, testing methods, shaft grounding brush replacement procedures and calibration tolerances.  In the event such manuals are not obtainable from the manufacturer, it shall be the responsibility of the Subcontractor to compile and include them.  Advertising brochures shall not be used in lieu of the required technical manuals.

          - Include revised schedules for each electrical panel modified for this project.

          - Statement of Guarantee including date of termination.

        - Name, address, and phone number of the service representative to be called in the event of equipment failure.

      - QUALITY ASSURANCE

        - Manufacturer Qualifications: Experienced in manufacturing the products specified in this Section with minimum five years documented product development, testing, and manufacturing experience.

      - Delivery, storage, and handling

        - Comply with Division 22 Section "Common Results for Plumbing", Part 1.15, Material Delivery.

        - Protect motors stored on site from weather and moisture by maintaining factory covers and suitable weather-proof covering.  For extended outdoor storage, remove motors from equipment and store separately.

      - SEQUENCING AND SCHEDULING

        - Coordinate work under provisions of Division 01 Section "General Requirements."

        - Coordinate installation of motors with other mechanical and electrical systems equipment being interfaced such as air handling units and motor control centers.

      - WARRANTY

        - Free maintenance services shall be provided by the Subcontractor for one (1) year after final system acceptance in accordance with Division 01 Section "General Requirements."  These services shall consist of manufacturer's factory-trained representatives providing emergency repair service with on-site response within 24 hours of call, all test equipment and hardware necessary for maintenance and repair work and installation of modifications designed to improve system performance or eliminate known problems or deficiencies.

        - During the warranty period, provide new or revised documentation showing all changes required to solve system problems.

        - Submit written reports on each service or inspection to the LBNL Project Manager during the warranty period.

- PRODUCTS

      - MANUFACTURERS

        - Baldor

        - Dayton

        - General Electric

        - Reliance

        - U.S. Motors

        - Westinghouse

      - GENERAL CONSTRUCTION AND REQUIREMENTS

        - Electrical Service:

          - Motors 1/4 HP and smaller: 115 volts, single phase, 60 Hz.

          - Motors 3/4 HP and smaller, annual operating hours less than 3,000: 115 volts, single phase, 60 Hz.

          - Motors 1/2 HP and larger, annual operating hours greater than 3,000: 460 volts, three phase, 60 Hz.

          - Motors larger than 3/4 Horsepower: 460 volts, three phase, 60 Hz.

        - Type:

          - Single-phase motors shall be split phase, permanent split capacitor, capacitor start, or capacitor start/capacitor run type as determined by the application.  Shaded pole motors are specifically prohibited.

          - Three-phase motors shall be open drip-proof or totally enclosed for indoor dry locations and shall be totally enclosed for outdoor or other wet locations.

          - Motors located in draw-through cooling towers:  Totally enclosed weatherproof epoxy-sealed type.

          - Design for continuous operation in 40°C environment.

          - Design for temperature rise in accordance with NEMA MG 1 limits for insulation class, service factor, and motor enclosure type.

        - Visible Nameplate: Indicate manufacturer's name, model number, serial number, horsepower, voltage, phase, frequency, RPM, full load amps, locked rotor amps or code, frame size, service factor, power factor, nominal full-load efficiency, bearing sizes, insulation class, and rated ambient temperature.

        - Wiring Terminations:

          - Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in terminal box sized to NFPA 70, threaded for conduit.

          - For fractional horsepower motors where connection is made directly, provide threaded conduit connection in end frame.

        - Explosion-Proof Motors: UL approved and labeled for hazard classification, with over-temperature protection.

      - SINGLE PHASE POWER - SPLIT PHASE MOTORS

        - Starting Torque: Less than 150 percent of full load torque.

        - Starting Current: Less than seven times full load current.

        - Breakdown Torque: Approximately 200 percent of full load torque.

        - Open Drip-proof Enclosure: Class A (50(C temperature rise) insulation, NEMA Service Factor, prelubricated sleeve or ball bearings.

        - Enclosed Motors: Class A (50(C temperature rise) insulation, 1.0 Service Factor, prelubricated ball bearings.

      - SINGLE PHASE POWER - PERMANENT-SPLIT CAPACITOR  MOTORS

        - Starting Torque: Capable of exceeding one fourth of full load torque.

        - Starting Current: Less than six times full load current.

        - Multiple Speed: Through tapped windings.

        - Open Drip-proof or Enclosed Air Over Enclosure: Class A (50(C temperature rise) insulation, minimum 1.0 Service Factor, prelubricated sleeve or ball bearings, automatic reset overload protector.

      - SINGLE PHASE POWER - CAPACITOR START MOTORS

        - Starting Torque: Capable of three times full load torque.

        - Starting Current: Less than five times full load current.

        - Pull-up Torque: Up to 350 percent of full load torque.

        - Breakdown Torque: Approximately 250 percent of full load torque.

        - Capacitor in series with starting winding; provide capacitor-start/capacitor-run motors with two capacitors in parallel with run capacitor remaining in circuit at operating speeds.

        - Open Drip-proof Enclosure: Class A (50(C temperature rise) insulation, NEMA Service Factor (see Section 3.03), prelubricated ball bearings.

        - Enclosed Motors: Class A (50(C temperature rise) insulation, 1.0 Service Factor, prelubricated ball bearings.

      - THREE PHASE POWER - SQUIRREL CAGE MOTORS

        - Starting Torque: Between 1 and 1-1/2 times full load torque.

        - Starting Current: Less than six times full load current.

        - Power Output, Locked Rotor Torque, Breakdown and Pull Out Torque: NEMA Design B characteristics.

        - Design, Construction, Testing, and Performance: Conform to NEMA MG 1 for Design B motors.

        - Insulation: NEMA Class F or better.

        - Testing Procedure: In accordance with IEEE 112B.  Load test motors to determine that they are free from electrical or mechanical defects in compliance with performance data.

        - Motor Frames: NEMA Standard Frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

        - Thermistor System (Motor Frame Sizes 284T and Larger): Three PTC thermistors imbedded in motor windings and epoxy encapsulated solid state control relay for wiring into motor starter; refer to Division 26 Section "Motor Control Centers."

        - Bearings: Grease lubricated anti-friction ball bearings with housings equipped with plugged provision for relubrication, rated for minimum AFBMA 9, L-10 life of 20,000 hours [L-50 life of 100,000 hours].  Calculate bearing load with NEMA minimum V-belt pulley with belt center line at end of NEMA standard shaft extension.  Stamp bearing sizes on nameplate.

        - Sound Power Levels: Motors shall conform to NEMA MG 1.

        - Part Winding Start where indicated: Use part of winding to reduce locked rotor starting current to approximately 60 percent of full winding locked rotor current while providing approximately 50 percent of full winding locked rotor torque.

        - Weatherproof Epoxy Sealed Motors: Epoxy seal windings using vacuum and pressure with rotor and stator surfaces protected with epoxy enamel; bearings double shielded with waterproof non-washing grease.

      - MOTOR EFFICIENCY

        - The manufacturer's nominal efficiency for the HP size specified shall be as shown in the Part 3 Schedules at 3/4 load and rated voltage when tested in accordance with IEEE 112B.

        - Motors 1/2 HP and smaller, with annual operating hours less than 3,000 may be the equipment manufacturer's standard and need not conform to these specifications.

      - MOTOR POWER FACTOR

        - The manufacturer's nominal power factor for the HP size specified shall be as shown in the Part 3 Schedules at 3/4 load and rated voltage when tested in accordance with IEEE 112B.

        - Motors 1/2 HP and smaller, with annual operating hours less than 3,000 may be the equipment manufacturer's standard and need not conform to these specifications.

      - SHAFT GROUNDING

        - All motors driven by a VFD shall include shaft grounding on the non-drive end of the motor.  Shaft ground to be installed by electrical subcontractor.  Shaft grounding kits to consist of brass or stainless steel brushes.

        - Manufacturer:  Shaft Grounding Systems or equal.

- EXECUTION

      - installation

        - Install in accordance with manufacturer's instructions.

        - Install securely on firm foundation.

        - Check line voltage and phase and ensure agreement with nameplate.

      - NEMA OPEN MOTOR SERVICE FACTOR SCHEDULE

HP	3600 RPM	1800 RPM	1200 RPM	900 RPM

1/6-1/3	1.35	1.35	1.35	1.35

1/2	1.25	1.25	1.25	1.25

3/4	1.25	1.25	1.15	1.15

1-200	1.15	1.15	1.15	1.15

      - PERFORMANCE SCHEDULE:  THREE PHASE - OPEN DRIP-PROOF

Minimum %	Minimum  %	 	 	Nominal	Power 	NEMA	Efficiency	Factor

HP	RPM(Syn)	Frame	3/4 Load	3/4 Load

1	1200	145T	80.0	72.0

1-1/2	1200	182T	85.8	73.0

2	1200	184T	87.4	75.0

3	1200	213T	89.5	60.0

5	1200	215T	90.3	65.0

7-1/2	1200	254T	91.7	73.0

10	1200	256T	91.9	74.0

15	1200	284T	92.8	77.0

20	1200	286T	93.1	78.0

25	1200	324T	94.2	74.0

30	1200	326T	94.4	78.0

40	1200	364T	94.8	77.0

50	1200	365T	95.0	79.0

60	1200	404T	95.4	82.0

75	1200	405T	95.5	80.0

100	1200	444T	95.7	80.0

125	1200	445T	95.9	78.8

150	1200	445T	96.1	85.0

200	1200	447T	96.2	85.0

1	1800	143T	84.7	72.5

1-1/2	1800	145T	85.5	72.5

2	1800	145T	86.8	73.5

3	1800	182T	90.2	73.5

5	1800	184T	91.4	74.1

7-1/2	1800	213T	92.0	78.3

10	1800	215T	92.2	78.3

15	1800	256T	93.3	78.4

20	1800	256T	94.0	80.4

25	1800	284T	94.5	85.0

30	1800	286T	94.7	84.9

40	1800	324T	94.9	84.9

50	1800	326T	95.1	85.1

60	1800	364T	95.5	83.8

75	1800	365T	95.6	85.0

100	1800	404T	95.7	81.9

125	1800	405T	96.0	84.5

150	1800	444T	96.2	84.0

200	1800	445T	96.4	82.0

1	3600	143T	79.5	77.2

1-1/2	3600	143T	83.3	72.5

2	3600	145T	85.3	83.8

3	3600	145T	87.0	87.8

5	3600	182T	89.8	81.8

7-1/2	3600	184T	90.4	83.0

10	3600	213T	91.3	84.0

15	3600	215T	92.0	85.0

20	3600	254T	92.5	84.8

25	3600	256T	93.6	91.8

30	3600	284T	93.9	85.3

40	3600	286T	94.5	80.0

50	3600	324T	93.6	93.6

60	3600	326T	94.3	87.6

75	3600	364T	94.5	92.8

100	3600	365T	95.0	82.0

125	3600	404T	95.4	87.1

150	3600	405T	95.4	90.4

200	3600	444T	95.4	85.0

      - PERFORMANCE SCHEDULE: THREE PHASE, TOTALLY ENCLOSED, FAN COOLED.

Minimum %	Minimum  %	 	 	Nominal	Power 	NEMA	Efficiency	Factor

HP	RPM(Syn)	Frame	3/4 Load	3/4 Load

1	1200	145T	80.0	72.0

1-1/2	1200	182T	85.8	73.0

2	1200	184T	87.4	75.0

3	1200	213T	89.5	60.0

5	1200	215T	90.3	65.0

7-1/2	1200	254T	91.7	73.0

10	1200	256T	91.9	74.0

15	1200	284T	92.8	77.0

20	1200	286T	93.1	78.0

25	1200	324T	94.2	74.0

30	1200	326T	94.4	78.0

40	1200	364T	94.8	77.0

50	1200	365T	95.0	79.0

60	1200	404T	95.4	82.0

75	1200	405T	95.5	80.0

100	1200	444T	95.7	80.0

125	1200	445T	95.9	78.8

150	1200	445T	96.1	85.0

200	1200	447T	96.2	85.0

1	1800	143T	84.7	72.5

1-1/2	1800	145T	85.5	72.5

2	1800	145T	86.8	73.5

3	1800	182T	90.2	73.5

5	1800	184T	91.4	74.1

7-1/2	1800	213T	92.0	78.3

10	1800	215T	92.2	78.3

15	1800	256T	93.3	78.4

20	1800	256T	94.0	80.4

25	1800	284T	94.5	85.0

30	1800	286T	94.7	84.9

40	1800	324T	94.9	84.9

50	1800	326T	95.1	85.1

60	1800	364T	95.5	83.8

75	1800	365T	95.6	85.0

100	1800	404T	95.7	81.9

125	1800	405T	96.0	84.5

150	1800	444T	96.2	84.0

200	1800	445T	96.4	82.0

1	3600	143T	79.5	77.2

1-1/2	3600	143T	83.3	72.5

2	3600	145T	85.3	83.8

3	3600	145T	87.0	87.8

5	3600	182T	89.8	81.8

7-1/2	3600	184T	90.4	83.0

10	3600	213T	91.3	84.0

15	3600	215T	92.0	85.0

20	3600	254T	92.5	84.8

25	3600	256T	93.6	91.8

30	3600	284T	93.9	85.3

40	3600	286T	94.5	80.0

50	3600	324T	93.6	93.6

60	3600	326T	94.3	87.6

75	3600	364T	94.5	92.8

100	3600	365T	95.0	82.0

125	3600	404T	95.4	87.1

150	3600	405T	95.4	90.4

200	3600	444T	95.4	85.0

      - VIBRATION

        - Statically and dynamically balance motors to a vibration displacement not to exceed 2 mils peak to peak.

        - See Division 22 Section "Testing and Maintenance of Plumbing."

END OF SECTION 220513