SECTION 220553 – IDENTIFICATION FOR PLUMBING PIPING AND EQUIPMENT

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Identify all installed mechanical distribution piping, mechanical equipment and components.

          - Cast-in-place concrete.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 09 Section "Painting" for identification painting.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - ASME –American Society of Mechanical Engineers:

          - ASME A 13.1  Scheme for the identification of piping systems

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing, Review of Materials" and Division 01 Section "General Requirements."

        - Submit list of wording, symbols, letter size, and color coding for mechanical identification.

        - Submit valve chart and schedule, including valve tag number, location, function, and valve manufacturer's name and model number.

        - Submit valve database as per Part 3.05 -Stenciling and Identification, D.3 - Valve Tags.

- PRODUCTS

      - ACCEPTABLE MANUFACTURERS

        - W. H. Brady or Westline products.

        - No substitutions.

      - MATERIALS

        - Color coding:  ASME A13.1 unless specified otherwise.

        - Plastic nameplates:  laminated two-layer plastic with engraved black letters on light, contrasting background color.

        - Plastic tags:  laminated three-layer (double-sided) plastic with engraved black letters on light, contrasting background color.  Tag size at least 1-1/2 inch (38 mm) diameter.

        - Stencils:  with clean-cut symbols and letters of following size:

| Outside Diameter of Insulation or Pipe | Color Field Length | Letter Height |
| --- | --- | --- |
| ¾ to 1-1/4 inches (9.5 to 31.7 mm) | 8 inches (200 mm) | ½ inch (13 mm) |
| 1-1/2 to 2 inches (38.1 to 50.8 mm) | 8 inches (200 mm) | ¾ inch (20 mm) |
| 2-1/2 to 2 inches (63.5 to 50.8 mm) | 12 inches (300 mm) | 1 ¼ inch (32 mm) |
| 8 to 10 inches (203.2 to 254 mm) | 24 inches (600 mm) | 2 ½ inch (64 mm) |
| Over 10 inches (254 mm) | 32 inches (800 mm) | 3 inches (75 mm) |
| Ductwork and equipment | --- | 2 ½ inch (64 mm) |

        - Stencil paint: semi-gloss enamel; in accordance with Division 09 Section "Painting".

        - Plastic pipe markers:  factory fabricated, flexible, semi-rigid plastic, preformed to fit around pipe or pipe covering; minimum information indicating flow direction arrow and fluid being conveyed.

          - Special gases shall be identified using markers with yellow background and black letters, direction arrow, and full chemical names and symbols.

        - Plastic-tape pipe markers:  flexible, vinyl-film tape with pressure-sensitive adhesive backing and printed markings.

- EXECUTION

      - PREPARATION

        - Degrease and clean surfaces to receive adhesive of identification materials.

        - Prepare surfaces in accordance with Division 09 Section "Painting" for stencil painting.

      - INSTALLATION

        - Plastic nameplates:  install with corrosion-resistant mechanical fasteners, or adhesive.

        - Plastic tags:  install with corrosion-resistant chain.

        - Stencil painting:  apply in accordance with Division 09 Section "Painting".

        - Plastic pipe markers:  install in accordance with manufacturer's instructions.

        - Plastic-tape pipe markers:  install completely around pipe in accordance with manufacturer's instructions.

        - Underground plastic pipe markers:  install 6 to 8 inches (150 to 200 mm) below finished grade, directly above buried pipe.

      - IDENTIFICATION SCHEDULE

        - Equipment:  identify air-handling units, pumps, heat-transfer equipment, tanks, and water-treatment devices with plastic nameplates.  Small devices, such as in-line pumps, may be identified with plastic tags.

        - Controls:  identify control panels and major control components outside of panels with plastic nameplates.

        - Valves:  identify valves in main and branch piping with tags.

        - Piping:  identify piping, concealed or exposed, with stenciled painting.  Tags may be used on small diameter piping.  Identify service, flow direction, and pressure.  Install in clear view and align with axis of piping.  Locate identification not more than 20 feet (6 m) apart on straight runs including risers and drops, adjacent to each valve and tee, at each side of penetration of structure or enclosure, and at each obstruction.

        - Ductwork:  identify ductwork with stenciled painting.  Identify as to air-handling unit number, and area served.  Locate identification at air-handling unit, at each side of penetration of structure or enclosure, and at each obstruction.

      - VALVE DATABASE

        - Provide specified valve database.

      - STENCILING AND IDENTIFICATION

        - Stencil each piece of new and existing equipment including pumps, fans, tanks, etc., with the equipment tags scheduled on the drawings.  Use minimum 2 inches (50 mm) high characters.

          - Stencil each duct leaving the mechanical room indicating fan unit, area(s), direction of flow, or room(s) served.

          - Stencil each duct branch leaving an air shaft at each floor with fan number, and identify it as a supply, exhaust, or return duct, and indicate direction of air flow.

        - Post a framed and typewritten schedule of all stencils, pipe markers, valve tags, and lubricants used, with identification, shall be framed and posted in the mechanical equipment room.

        - Identify all pipes with specified markers.

          - Install markers every 10 feet (3 m) on mains, at all branch take-offs and adjacent to valves and cocks.

          - Apply to all exposed pipes, pipes behind removable tile ceiling, pipes in concealed but accessible locations, such as behind access panels and at least once in each room.

          - Install pipe marker using pressure sensitive adhesive in accordance with the manufacturer's directions.  The marker shall completely cover the circumference of the pipe and overlap itself.

        - Valve Tags:  Provide numbered tags for main valves, branch valves, zone valves, shut-off valves, and balancing valves installed under this Contract, constructed of #18 gauge (1.02 mm) brass, circular, 1 ¼ inches (31.7 mm) in diameter, and with numbers cut in and blackened so as to be plainly discernible.  Fasten tags to valve with brass links.

          - Valve numbers not required for valves obviously serving equipment such as air handler coils, reheat coil valves, and miscellaneous drains.

          - On the as-built drawings, indicate the location and number of each tagged valve.

          - Provide a computer file database in a form agreeable to the University, describing the valve, number, location , type of service normally “open” or “closed”, specific duty of each tagged valve, and manufacturer and model number.

        - Warning Sign at Fume Exhaust Plenums:  Place warning sign on each fume exhaust plenum access - "WARNING.  HAZARDOUS ATMOSPHERE INSIDE.  USE BREATHING APPARATUS" when breaching containment.

        - Place warning signs on all machines driven by electric motors which are controlled by fully automatic starters.  See Section 3320, Article 7, Subchapter 7, General Industry Safety Orders, Title 8, California Code of Regulations.

        - Fire dampers and fire smoke dampers:  at each fire damper or fire smoke damper access panel, label "FIRE DAMPER" or “FIRE SMOKE DAMPER” in minimum 2 inches (25 mm) high letters.  Fire smoke dampers shall be provided with tags to identify each fire smoke dampers as “FSD-NUMBER SEQUENCES-BLDG NUMBER”.  Provide chart to University for approval.

        - Wherever charts, Shop Drawings, etc. Refer to specific room numbers, use room numbers that will be provided by the university rather than the room numbers indicated on the Drawings.

END OF SECTION 220553