SECTION 220719 – PLUMBING PIPING INSULATION

- GENERAL

      - SUMMARY

        - Related Documents:/2rawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Piping insulation.

          - Jackets and accessories.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 09 Section "Painting" for painting insulation jacket".

          - Division 22 Section "Identification for Plumbing Piping and Equipment".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - ASTM International:

          - ASTM-B-209	Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

          - ASTM-C-195	Standard Specification for Mineral Fiber Thermal Insulating Cement

          - ASTM C 196	Standard Specification for Expanded or Exfoliated Vermiculite Thermal Insulating Cement

          - ASTM-C-449 	Standard Specification for Mineral Fiber Hydraulic-Setting Thermal Insulating and Finishing Cement

          - ASTM-C-533	Standard Specification for Calcium Silicate Block and Pipe Thermal Insulation

          - ASTM C534 / C534M 	Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

          - ASTM-C-547	Standard Specification for Mineral Fiber Pipe Insulation

          - ASTM-C-552	Standard Specification for Cellular Glass Thermal Insulation

          - ASTM C553	Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications

          - ASTM-C-578	Standard Specification for Rigid, Cellular Polystyrene Thermal Insulation

          - ASTM-C-610	Standard Specification for Molded Expanded Perlite Block and Pipe Thermal Insulation

          - ASTM-E-84	Standard Test Method for Surface Burning Characteristics of Building Material.

          - ASTM C 450	Standard Practice for Fabrication of Thermal Insulating Fitting Covers for NPS Piping, and Vessel Lagging

          - ASTM C 921	Standard Practice for Determining the Properties of Jacketing Materials for Thermal Insulation

          - ASTM B 209 	Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

          - ASTM A666	Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar

        - Code of Federal Regulations 20-CFR-1910.7 Definitions and Requirements for A Nationally Recognized Testing Laboratory (NRTL)

        - National Fire Protection Association NFPA-90A & NFPA-255 Surface Burning Characteristics of Building Materials

        - Underwriters Laboratories UL-723 Surface Burning Characteristics of Building Materials

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing, Review of Materials and Division 01 Section "General Requirements."

        - Subcontractor shall submit the product description, list of materials and thickness for each service, and at each location.

        - LEED Submittals:

          - Product Data for Credit EQ 4.1:  For solvent cements and adhesive primers, including printed statement of VOC content.

      - QUALITY ASSURANCE

        - Subcontractor shall assure applicator is a company specializing in piping insulation application with at least 3-years relevant experience.

        - Fire Hazard:  Provide insulation, jackets, facings adhesives and accessories acceptable to the State Fire Marshal, and meeting the requirements of NFPA 90A.  Meet the following hazard classifications stated in accordance with U.L. Test Method of Fire Hazard Classifications of Building Materials, No. 723:

          - Flame-spread:  Maximum 25.

          - Fuel Contributed:  Maximum 50.

          - Smoke Developed:  Maximum 50.

- PRODUCTS

      - ACCEPTABLE MANUFACTURERS

        - Manville Corporation, Certain-Teed, or Owens Corning Fiberglass.

        - Armacell (Armaflex Cellucar Insulation) LLC.

        - No substitutions

      - INSULATION MATERIALS

        - Mineral-Fiber Insulation:  Glass fibers bonded with a thermosetting resin complying with the following:

          - Preformed Pipe Insulation:  Comply with ASTM C 547, Type I, with factory-applied, all-purpose, vapor-retardant jacket.

          - Blanket Insulation:  Comply with ASTM C553, Type II, without facing.

          - Fire-Resistant Adhesive:  Comply with MIL-A-3316C in the following classes and grades:

            - Class I, Grade A for bonding glass cloth and tape to unfaced glass-fiber insulation, for sealing edges of glass-fiber insulation, and for bonding lagging cloth to unfaced glass-fiber insulation.

            - Class 2, Grade A for bonding glass-fiber insulation to metal surfaces.

            - For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

          - Vapor-Retarder Mastics:  Fire and water-resistant, vapor-retarder mastic for indoor applications. Comply with MIL-C 19565C, Type II.  See Section 2.5 below.

          - Mineral-Fiber Insulating Cements:  Comply with ASTM C 195.

          - Expanded or Exfoliated Vermiculite Insulating Cements:  Comply with ASTM C 196.

          - Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement:  Comply with ASTM C 449/C 449M.

        - Cellular-Glass Insulation:  Inorganic, foamed or cellulated glass, annealed, rigid, hermetically sealed cells, incombustible.

          - Preformed Pipe Insulation, without Jacket:  Comply with ASTM C 552, Type II, Class I.

          - Preformed Pipe Insulation, with Jacket:  Comply with ASTM C 552, Type II, Class 2.

          - Cellular-Glass, Phenolic, Polyisocyanurate, and Polystyrene Adhesive:  Solvent-based resin adhesive, with a service temperature range of minus 75 to plus 300 deg F.  For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

        - Prefabricated Thermal Insulating Fitting Covers:  Comply with ASTM C 450 for dimensions used in performing insulation to cover valves, elbows, tees, and flanges.

      - FIELD-APPLIED JACKETS

        - General:  ASTM C 921, Type I, unless otherwise indicated.

        - Foil and Paper Jacket:  Not acceptable.

        - PVC Jacket:  High-impact, ultraviolet-resistant PVC; 20 mils thick; roll stock ready for shop or field cutting and forming.

          - Adhesive:  As recommended by insulation material manufacturer.

          - PVC Jacket Color:  White

          - PVC Jacket Color:  Color-code piping jacket as determined by existing conditions.

          - Not to be used for outdoors.

        - Heavy PVC Fitting Covers:  Factory-fabricated fitting covers manufactured from 30-mil (0.75 mm) thick, high-impact, ultraviolet-resistant PVC.

          - Shapes:  45 and 90-degree, short and long-radius elbows, tees, valves, flanges, reducers, end caps, soil-pipe hubs, traps, mechanical joints, and P-trap and supply covers for lavatories for the disabled.

          - Adhesive:  As recommended by insulation material manufacturer.

          - Not to be used for outdoors.

        - Aluminum Jacket:  Aluminum roll stock, ready for shop or field cutting and forming to indicated sizes. Comply with ASTM B 209 (ASTM B 209M), 3003 alloy, H-14 temper.

          - Finish and Thickness:  Smooth finish, 0.010 (0.25 mm) inch thick.

          - Moisture Barrier:  1-mil thick, heat-bonded polyethylene and kraft paper.

          - Elbows:  preformed 45 and 90-degree, short and long-radius elbows; same material, finish, and thickness as jacket.

      - ACCESSORIES AND ATTACHMENTS

        - Bands: stainless steel ASTM A666, Type 304, 3/4 inch (20 mm) wide; 0.02 inch (0.050 mm) thick.

      - VAPOR RETARDANTS

        - Mastics:  Use materials as recommended by the insulation material manufacturer that are compatible with insulation materials, jackets, and substrates.

        - Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-C-19565C, Type II.

          - For indoor applications, use mastics that have a VOC content of <Insert value> g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

      - SEALANTS

        - Joint Sealants:

          - For indoor applications, use mastics that have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation and other conditions affecting performance of insulation application.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Install materials after piping has been tested and approved.

        - Surface Preparation:  Clean and dry surfaces to receive insulation. Remove materials that will adversely affect insulation application.

      - General application requiremenTs.

        - Apply insulation materials, accessories, and finishes according to the manufacturer's written instructions; with smooth, straight, and even surfaces; and free of voids throughout the length of ducts and fittings.

        - Refer to schedules at the end of this Section for material, form, jacket, and thickness required for each piping system insulation requirements.

        - Use accessories compatible with insulation materials and suitable for the service.  Use accessories that do not corrode, soften or otherwise attack insulation or jacket when in either wet or dry state.

        - Apply insulation with longitudinal seams at top and bottom of horizontal pipe runs.

        - Apply multiple layers of insulation with longitudinal and end seams staggered.

        - Do not weld brackets, clips, or other attachment devices to piping, fittings, and specialties.

        - Seal joints and seams with vapor-retardant mastic on insulation indicated to receive a vapor retardant.

        - Keep insulation materials dry during application and finishing.

        - Apply insulation with tight longitudinal seams and end joints. Bond the seams and joints with adhesive recommended by the insulation material manufacturer.

        - Apply insulation with the least number of joints practical.

        - Apply insulation over fittings, valves, and specialties, with continuous thermal and vapor-retardant integrity, unless otherwise indicated. Refer to special instruction for applying insulation over fittings, valves, and specialties.

        - Hangers and Anchors:  Where vapor retardant is indicated, seal penetrations in insulation at hangers, supports, anchors, and other projections with vapor-retardant mastic.

          - Apply insulation continuously through hangers and around anchor attachments.

          - For insulation application where vapor retardants are indicated, extend insulation on anchor legs at lease 12 inches (300 mm)es from point of attachment to pipe and taper insulation ends. Seal tapered ends with a compound recommended by the insulation material manufacturer to maintain vapor retardant integrity.

          - Install insert materials and apply insulation to tightly join the insert. Seal insulation to insulation inserts with adhesive or sealing compound recommended by the insulation material manufacturer.

          - Cover inserts with jacket material matching adjacent pipe insulation. Install shields over jacket, arranged to protect the jacket from tear or puncture by the hanger, support, and shield.

        - Insulation Terminations:  For insulation where vapor retardants are indicated, taper insulation ends. Seal tapered ends with a compound recommended by the insulation material manufacturer to maintain vapor retardant integrity.

        - Apply adhesives and mastics at the manufacturer's recommended coverage rate.

        - Apply insulation with integral jackets as follows:

          - Pull jacket tight and smooth.

          - Circumferential Joints:  Cover with 3 inches (75 mm) wide strips, of same material as insulation jacket. Secure strips with adhesive and outward clinching staples along both edges of strip and spaced 4-inches o.c.

          - Longitudinal Seams:  Overlap jacket seams at least 1 1/2 inches (38 mm). Apply insulation with longitudinal seams at bottom of pipe. Clean and dry surface to receive self-sealing lap. Staple laps with outward clinching staples along edge at 4-inches o.c.

          - Exception:  Do not staple longitudinal laps on insulation having a vapor retardant.

          - Vapor-retardant mastics:  Where vapor retardants are indicated, apply mastic on seams and joints and at ends adjacent to flanges, unions, valves, and fittings.

          - At penetrations in jackets for thermometers and pressure gauges, fill and seal voids with vapor-retardant mastic.

        - Roof Penetrations:  Apply insulation for interior applications to a point even with top of roof flashing.

          - Seal penetrations with vapor-retardant mastic.

          - Apply insulation for exterior applications tightly joined to interior insulation ends.

          - Extend metal jacket for exterior insulation occurring outside of roof flashing at least 2-inches below the top of the roof flashing.

          - Seal sheet metal jacket to roof flashing with vapor-retardant mastic.

        - Exterior Wall Penetrations:  For penetration of below-grade exterior walls, terminate insulation flush with mechanical sleeve seal. Seal terminations with vapor-retardant mastic.

        - Interior Wall and Partition Penetrations:  Apply insulation continuously through walls and floors.

        - Fire-Rated Wall and Partition Penetrations:  Apply insulation continuously through penetrations of fire-rated walls and partitions

          - Firestopping and fire-resistive joint sealers are specified in Division 07 "Penetration Firestopping".

          - Floor Penetrations:  Apply insulation continuously through floor assembly.

          - For insulation with vapor retardants, seal insulation with vapor-retardant mastic where floor supports penetrate vapor retardant.

      - MINERAL-FIBER INSULATION APPLICATION

        - Apply insulation to straight pipes and tubes as follows;

          - Secure each layer of preformed pipe insulation to pipe with wire, tape, or bands without deforming insulation materials.

          - Where vapor retarders are indicated, seal longitudinal seams and end joints with vapor-retarder mastic. Apply vapor retarder to ends of insulation at intervals of 15 to 20-feet (4.5 to 6 m) to form a vapor retarder between pipe insulation segments.

          - For insulation with factory-applied jackets, secure laps with outward clinches staples at 6 inches o.c.

          - For insulation with factory-applied jackets with vapor retarders, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by the insulation material manufacturer and seal with vapor-retarder mastic.

        - Apply Insulation to flanges as follows:

          - Apply preformed pipe insulation to outer diameter of pipe flange.

          - Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

          - Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with mineral-fiber blanket insulation.

          - Apply canvas jacket material with manufacturer's recommended adhesive, overlapping seams at least 1 inch (25 mm), and seal joints with vapor-retarder mastic.

        - Apply insulation to fittings and elbows as follows:

          - Apply premolded insulation sections of the same material as straight segments of pipe insulation when available. Secure according to manufacturer's written instructions.

          - When premolded insulation elbows and fittings are not available, apply mitered sections of pipe insulation, or glass-fiber blanket insulation, to a thickness equal to adjoining pipe insulation. Secure insulation materials with wire, tape, or bands.

          - Cover fittings with heavy PVC covers. Overlap PVC covers on pipe insulation jackets at least 1 inch (25 mm) at each end. Secure fitting covers with manufacturer's attachments and accessories. Seal seams with tape and vapor-retarder mastic.

        - Apply insulation to valves and specialties as follows:

          - Apply premolded insulation sections of the same material as straight segments of pipe insulation when available. Secure according to manufacturer's written instructions.

          - When premolded insulation sections are not available, apply glass-fiber blanket insulation to valve body. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation. For check valves, arrange insulation for access to strainer basket without disturbing insulation.

          - Apply insulation to flanges as specified for flange insulation application.

          - Use preformed heavy PVC fitting covers for valve sizes where available. Secure fitting covers with manufacturer's attachments and accessories. Seal seams with tape and vapor-retarder mastic.

          - For larger sizes where PVC fitting covers are not available, seal insulation with canvas jacket and sealing compound recommended by the insulation material manufacturer.

      - CELLULAR-GLASS INSULATION APPLICATION

        - Apply insulation to straight pipes and tubes as follows:

          - Secure each layer of insulation to pipe with bands without deforming insulation.

          - Where vapor retarders are indicated, seal longitudinal seams and end joints with vapor-retarder mastic.

          - For insulation with factory-applied jackets, secure laps with outward clinched staples at 6-inches o.c.

          - For insulation with factory-applied jackets with vapor retarders, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by the insulation material manufacturer and seal with vapor-retarder mastic.

        - Apply insulation to flanges as follows:

          - Apply preformed pipe insulation to outer diameter of pipe flange.

          - Make width of insulation segment the same as overall width of the flange and bolts, plus twice the thickness of the pipe insulation.

          - Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of cellular-glass block insulation of the same thickness as pipe insulation

          - Apply insulation to fittings and elbows as follows:

          - Apply premolded insulation sections of the same material as straight segments of pipe insulation when available. Secure according to manufacturer's written instruction.

          - When premolded sections of insulation are not available, apply mitered sections of cellular-glass insulation. Secure insulation materials with bands.

          - Cover fittings with heavy PVC fitting covers. Overlap PVC covers on pipe insulation jackets as least 1 inch (25 mm) at each end. Secure fitting covers with manufacturer's attachments and accessories. Seal seams with tape and vapor-retarder mastic.

        - Apply insulation to valves and specialties as follows:

          - Apply premolded segments of cellular-glass insulation or glass-fiber blanket insulation to valve body. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation. For check valves, arrange insulation for access to strainer basket without disturbing insulation.

          - Apply insulation to flanges as specified for flange insulation application.

          - Use preformed heavy PVC fitting covers for valve sizes where available. Secure fitting covers with manufacturer's attachments and accessories. Seal seams with tape and vapor-retarder mastic.

          - For larger sizes where PVC fitting covers are not available, seal insulation with canvas jacket and sealing compound recommended by the insulation material manufacturer.

      - PREFORMED ELASTOMERIC CELLULAR THERMAL INSULATION APPLICAION

        - Apply insulation to straight pipes and tubes as follows:

          - Install pipe insulation by slitting tubular sections and applying onto pipes.  Seams and butt joints shall be adhered and sealed using Armaflex 520 adhesive

          - All edges shall be clean-cut.  Rough or jagged edges shall not be permitted.

        - Apply insulation to valves, flanges and fittings as follows:

          - Insulate with the same insulation thickness as the adjacent piping. Seams and butt joints shall be adhered and sealed with Armaflex 520 adhesive.

          - All edges shall be clean-cut.  Rough or jagged edges shall not be permitted.

        - Outdoor insulation shall be protected as follows:

          - Furnish PVC jacket and PVC fitting covers or aluminum jackets.

          - All jackets shall have the seams located on the bottom of the pipes.

      - FIELD-APPLIED JACKET APPLICATION

        - Apply PVC jacket where indicated, with 1 inch (25 mm) overlap at longitudinal seams and end joints. Seal with manufacturer's recommended adhesive.

        - Apply metal jacket where indicated, with 2-inch (50 mm) overlap at longitudinal seams and end joints. Overlap longitudinal seams arranged to shed water. Seal end joints with weatherproof sealant recommended by insulation manufacturer. Secure jacket with stainless-steel band 12 inches (300 mm)es o.c. and at end joints.

        - Insulation and jacket for cold pipes shall include wicks to direct possible condensation to outside the jacket.  The product shall be Knauf PermaWick or equal.

        - Indoor, Concealed Applications:  Insulated pipes conveying fluids above ambient temperature shall have standard jackets, with or without vapor barrier, factory-applied or field-applied.  Insulate fittings, joints and valves with insulation of like material and thickness as adjoining pipe, and finish with glass cloth and adhesive.  PVC jackets shall be used.

        - Indoor, Exposed Applications:  For pipe exposed in mechanical equipment rooms or in finished spaces, insulate as for concealed applications.  Finish with canvas jacket; size for finish painting.  PVC jackets shall be used.

        - Exterior Applications:  Provide vapor-barrier jackets.  Cover with aluminum jacket with seams located on bottom side of horizontal piping.  Insulate fittings, joints, and valves with insulation of like material and thickness as adjoining pipe, and cover with aluminum jacket.

        - Buried Piping:  Provide factory-fabricated assembly with inner all-purpose service jacket with self-sealing lap, and asphalt-impregnated open-mesh glass fabric, with 0.001 inch thick aluminum foil sandwiched between three layers of bituminous compound; outer surface faced with a polyester film.

      - FINISHES

        - Paint insulation as specified in Division 09 Section "Painting".

        - Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

      - PIPING SYSTEM APPLICATIONS

        - Insulation materials and thicknesses are specified in schedules at the end of this Section.

        - Items Not Insulated: Unless otherwise indicated, do not apply insulation to the following systems, materials, and equipment.

          - Flexible connectors.

          - Vibration control devices.

          - Fire-suppression piping.

          - Drainage piping located in crawl spaces, unless otherwise indicated.

          - Below-grade piping, unless otherwise indicated.

          - Chrome-plated pipes and fittings, unless potential for personal injury.

          - Air chambers, unions, strainers, check valves, plug valves, and flow regulators.

      - INSULATION APPLICATION SCHEDULE, GENERAL.

        - Refer to insulation application schedules for required insulation materials, vapor retarders, and field-applied jackets.

        - Application schedules identify piping system and indicate pipe size ranges and material, thickness, and jacket requirements.

      - INTERIOR INSULATION APPLICATION SCHEDULE

        - Service:  Domestic and Industrial hot water.203.2 mm

          - Operating Temperature:  60 to 140 deg F (15.6 to 60 deg C).

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Copper Pipe, Up to 2 inches (50.8 mm):  1 inch (25 mm) Insulation

          - Field-Applied Jacket:  PVC

          - Vapor Retarder Required:  Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Chilled-water supply and return.

          - Operating Temperature:  35 to 75 deg F (2 to 24 deg C).

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Steel Pipe, All sizes:  1 inch (25 mm) Insulation

            - Copper All sizes:  1 inch (25 mm) Insulation

          - Field-Applied Jacket:  PVC

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Heating hot-water supply and return.

          - Operating Temperature:  100 to 200 deg F (38 to 93 deg C).

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Steel Pipe, Up to 2 inches (50.8 mm):  1 inch (25 mm) Insulation

            - Copper Pipe, Up to 2 inches (50.8 mm):  1 inch (25 mm) Insulation

            - Steel Pipe, 2 1/4 inches (57.2 mm) to 6 inches (152.4 mm):  1 1/2 inch (38 mm) Insulation

            - Copper Pipe, 2 1/4 inches (57.2 mm) to 6 inches (152.4 mm):  1 1/2 inch (38 mm) Insulation

          - Field-Applied Jacket:  PVC

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Steam and Condensate:

          - Operating Temperature:  450 deg F (232 deg C) and lower

          - Insulation Material:  Mineral-fiber or Calcium Silicate

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Steel Pipe, Steam Up to 2 inches (50.8 mm):  1 1/2 inch (38 mm) Insulation

            - Steel Pipe, Steam 2 1/4 inches (57.2 mm) to 4 inches (101.6 mm):  3 inches (75 mm) Insulation

            - Steel Pipe, Condensate Up to 2 inches (50.8 mm) :  1 1/2 inch (38 mm) Insulation

          - Field-Applied Jacket:  Aluminum

          - Vapor Retarder Required:  No

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Process Cold Water - (Industrial):

          - Operating Temperature:  30 deg F (1.1 deg C)

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness: Apply the following insulation thicknesses:

            - Copper Pipe, All Sizes:  1 inch (25 mm) Insulation

          - Field-Applied Jacket:  PVC

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

      - EXTERIOR INSULATION APPLICATION SCHEDULE

        - This application schedule is for aboveground insulation outside the building.

        - Service:  Domestic, industrial and DI Water.

          - Operating Temperature:  60 to 140 deg F (15 to 60 deg C).

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Copper pipe, All sizes:  1 inch (25 mm) Insulation

            - Polypropylene Pipe 1 inch (25 mm) Insulation

          - Field-Applied Jacket:  Aluminum

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Chilled-water supply and return.

          - Operating Temperature:  35 to 75 deg F (2 to 24 deg C).

          - Insulation Material:  Mineral-fiber

          - Insulation Thickness: Apply the following insulation thicknesses:

            - Steel pipe, All sizes:  1 1/2 inch (38 mm) Insulation

            - Copper Pipe, All sizes:  1 1/2 inch (38 mm) Insulation

          - Field-Applied Jacket:  Aluminum

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Heating hot-water supply and return.

          - Operating Temperature:  100 to 220 deg F (38 to 104 deg C)

          - Insulation Material:  Mineral Fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Steel Pipe, All sizes:  1 1/2 inch (38 mm) Insulation

            - Copper Pipe, All sizes:  1 1/2 inch (38 mm) Insulation

          - Field-Applied Jacket:  Aluminum

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

        - Service:  Steam and condensate.

          - Operating Temperature:  450 deg F (232 deg C) and lower.

          - Insulation Material:  Mineral Fiber

          - Insulation Thickness:  Apply the following insulation thicknesses:

            - Steel Pipe, Steam Up to 2 inches (50.8 mm):  2 1/2 inch (63 mm) Insulation

            - Steel Pipe, Steam 2 1/4 inches (57.2 mm) to 8 inches (203.2 mm):  3 1/2 inch (89 mm) Insulation

            - Steel Pipe, Condensate Up to 2 inches (50.8 mm):  1 1/2 inch (38 mm) Insulation

            - Steel Pipe, Condensate 2 1/4 inches (57.2 mm) to 8 inches (203.2 mm):  2 inches (50.8 mm) Insulation

          - Field-Applied Jacket:  Aluminum

          - Vapor Retarder Required: Yes

          - Finish:  As specified in Paragraph 3.8.

      - ALTERNATE INSULATION APPLICATION

        - Preformed elastomeric cellular insulation may be used as an alternative to the materials in Sections 3.12 and 3.13.

END OF SECTION 220719