SECTION 223000 – PLUMBING EQUIPMENT

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Water heaters.

          - Packaged water heating systems.

          - Heat exchangers.

          - Water storage tanks.

          - Underground fuel storage tank.

          - Pumps.

          - Pressure booster system.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment".

          - Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - American Society of Mechanical Engineers (ASME):

          - ASME Section 8D - Pressure Vessels

        - National Fire Protection Association (NFPA)

          - NFPA 30 	Flammable and Combustible Liquids

          - NFPA 31	Installation of Oil Burning Equipment

          - NFPA 54 	National Fuel Gas Code

          - NFPA 58 	Storage and Handling of Liquefied Petroleum Gases

          - NFPA 70 	National Electrical Code

        - Underwriters Laboratories Inc. (UL):

          - UL 174 	Household Electric Storage Tank Water Heaters

          - UL 1453 	Electric Booster and Commercial Storage Tank Water Heaters

- <AGA certifies gas-fired water heaters.  NSF certifies heaters for dishwasher supply water.  ASME is usually used in commercial, institutional, or industrial applications.>

        - Conform to [AGA] [NSF] [NBBPVI] [NFPA 54] [NFPA 58] [NFPA 70] [UL 174] [UL 1453] requirements for water heaters.

        - Conform to ASME Section 8D for manufacture of pressure vessels for heat exchangers.

        - Conform to [ASME Section 8D] [NFPA 30] [NFPA 31] for tanks.

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing, Review of Materials" and Division 01 Section "General Requirements."

        - LEED Submittals:

          - Product Data for Prerequisite EA 2:  Documentation indicating that units comply with ASHRAE/IESNA 90.1-2004, Section 7 - "Service Water Heating."

        - Submit [Shop Drawings and] Product Data:

          - Include dimension drawings of water heaters indicating components and connections to other equipment and piping.

          - Include heat-exchanger dimensions, size of tappings, and performance data.

          - Include dimensions of tanks, tank lining methods, anchors, attachments, lifting points, tappings, and drains.

          - Indicate pump type, capacity, power requirements, and affected adjacent construction.

        - Submit certified pump curves showing pump-performance characteristics with pump and system operating point plotted.  Include NPSH curve when applicable.

- <When manufacturer’s instructions for specific installation requirements are used, carefully edit PART 3 requirements to avoid conflicts with those instructions.>

        - Submit manufacturer’s installation instructions.

        - Submit manufacturer’s certificate that pressure vessels meet or exceed [specified requirements] [     ].

        - Submit manufacturer’s certificate that [     ] pumps meet or exceed [specified requirements] [     ].

        - Operation and Maintenance Data:  Include operation, maintenance, and inspection data, replacement part numbers and availability, and service depot location and telephone number.

      - QUALITY ASSURANCE

        - Provide pumps with manufacturer’s name, model number, and rating/capacity identified.

        - ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004.

        - Ensure that products and installation of specified products are in conformance with recommendations and requirements of the following organizations:

          - American Gas Association (AGA)

          - National Sanitation Foundation (NSF)

          - American Society of Mechanical Engineers (ASME)

          - National Board of Boiler and Pressure Vessel Inspectors (NBBPVI)

          - National Electrical Manufacturers’ Association (NEMA)

          - Underwriters Laboratories (UL)

        - Ensure that pumps operate at specified system fluid temperatures without vapor binding and cavitation, are non-overloading in parallel or individual operation, and operate within 25 percent of midpoint of published maximum efficiency curve.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver to site, store, and protect products.

        - Provide temporary inlet and outlet caps.  Maintain caps in place until installation.

      - WARRANTY

- <Consider this Article carefully.  Most commercial equipment carries a 1-year warranty only.  Nonprorated warranties are not common on smaller equipment, particularly of domestic quality.>

        - Provide [5] [     ]-year [manufacturer’s] [nonprorated] warranty.

        - Warranty:  Include coverage of [domestic water heaters] [water storage tanks] [packaged water heating systems] [in-line circulator] [submersible sump pumps] [sump pumps] [sewage ejectors].

- PRODUCTS

      - ACCEPTABLE MANUFACTURERS - WATER HEATERS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - RESIDENTIAL GAS FIRED WATER HEATER

- <Include performance here if only one type or size of heater is to be specified.  Delete and use schedule at end of section for more than one type or size of unit.>

        - A.	Automatic, natural gas-fired, vertical storage type, [with [gallons (liters)] capacity, [     ]-Btu/hr input, minimum recovery rate [     ]-gpm (L/s) with 100 deg F (37.7 deg C) temperature rise,] 150 psig (1035 kPa) maximum working pressure.

        - Household, Atmospheric, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

          - Factory-Installed, Storage-Tank Appurtenances:

            - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Household, Direct-Vent, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

          - Factory-Installed, Storage-Tank Appurtenances:

            - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Household, Power-Vent, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

          - Factory-Installed, Storage-Tank Appurtenances:

- a. Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Glass-lined welded-steel tank; single-flue passage, flue baffle and draft hood; thermally insulated with glass fiber and encased in corrosion-resistant steel jacket; baked-enamel finish; floor shield and legs.

        - Automatic water thermostat and built-in gas-pressure regulator; temperature range adjustable from 120 to 170 deg F (48.9 to 76.7 deg C), cast-iron or sheet-metal burner, safety pilot and thermocouple.

- <Temperature and pressure relief valves for residential units are not necessarily ASME certified and labeled.>

        - Brass water connections and dip tube, drain valve, high-density magnesium anode, and temperature- and pressure-relief valve.

      - COMMERCIAL GAS FIRED WATER HEATER

- <Include performance here if only one type or size of heater is to be specified.  Delete and use schedule at end of section for more than one type or size of unit.>

        - Automatic, natural-gas-fired, vertical-storage type, [with [     ]-gal capacity, [     ]-Btu/hr input, minimum recovery rate [     ] gpm (L/s) with 100 deg F (37.7 deg C) temperature rise,] 150 psig (1035 kPa) maximum working pressure.

- <Copper-lined tanks should only be considered when water conditions dictate their use.>

        - [Glass-lined] [Copper-lined] welded steel tank; multiple flue passages, 4 inches (100 mm) diameter inspection port, thermally insulated with at least 2 inches (50mm) of glass fiber, encased in corrosion-resistant steel jacket; baked-enamel finish; floor shield and legs.

        - Brass water connections and dip tube, drain valve, high-density magnesium anode, and ASME-rated temperature- and pressure-relief valve.

- <Most commercial units are approved for applications listed.>

        - Unit approved by AGA as automatic storage-tank water heater and [automatic circulating-tank water heater] [for] [operation at 180 F] [operation on combustible floors] [high-altitude installation].

        - Automatic water thermostat with temperature range adjustable from 120 to 180 F, gas pressure regulator, multi-ribbon or tubular burner, 100 percent safety shut-off pilot and thermocouple, flue baffle and draft hood.

- <Use the following control system for units with less than 400,000 Btu/hr input.>

        - Automatic direct-immersion thermostat with temperature range adjustable over at least 175 F differential, automatic-reset high-temperature-limiting thermostat factory set at 205 F, gas-pressure regulator, multi-ribbon or tubular burner, 100 percent safety shut-off pilot and thermocouple, [intermittent electronic-ignition-monitoring pilot and main flame, trial for reignition for momentary loss of flame, shutdown of pilot and main burner in 2–4 seconds after loss of flame,] [and] [automatic flue damper] [,] [and power venter].

      - RESIDENTIAL ELECTRIC WATER HEATER

- <Include performance here if only one type or size of heater is to be specified.  Delete and use schedule at end of section for more than one type or size of unit.>

        - A.	Automatic, electric, vertical storage type, [     ]-gal capacity, [     ]-kW input, recovery rate [     ] gal/hr with 100 deg F (37.7 deg C)  temperature rise,] 150 psig (1035 kPa) maximum working pressure.

        - Household, Small-Capacity Electric Water Heaters:  Comply with UL 174.

          - Factory-Installed Storage-Tank Appurtenances:

            - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Household, [Standard] [Tabletop], Storage Electric Water Heaters:  Comply with UL 174.

          - Factory-Installed Storage-Tank Appurtenances:

            - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Household, Collector-to-Tank, Solar-Electric Water Heaters:  Comply with UL 174 with piping and electrical connections for UL 1279 solar collector system.

          - Factory-Installed Storage-Tank Appurtenances:

            - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Household, Collector-to-Tank, Heat-Exchanger-Coil, Solar-Electric Water Heaters:  Comply with UL 174 with integral coil-type heat exchanger.

          - Factory-Installed Storage-Tank Appurtenances:

        - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

        - Glass-lined welded-steel tank, thermally insulated with [2] [3]-inch thick glass fiber; encased in corrosion-resistant steel jacket; baked-enamel finish.

        - Automatic water thermostat with [externally adjustable] temperature range from 120 to 170 deg F (48.8 to 76.6 deg C), flanged or screw-in nichrome elements, enclosed controls [,] [and] electrical junction box [,] [and operating light].

- <Temperature and pressure relief valves for residential units are not necessarily ASME certified and labeled.>

        - Brass water connections and dip tube, drain valve, high-density magnesium anode, and temperature- and pressure-relief valve.

      - COMMERCIAL ELECTRIC WATER HEATERS

        - Description:  Comply with UL 174 for household, storage electric water heaters.

        - Factory-Installed Storage-Tank Appurtenances:

          - Insulation:  Comply with ASHRAE/IESNA 90.1-2004.

- <Include performance here if only one type or size of heater is to be specified.  Delete and use schedule at end of section for more than one type or size of unit.>

        - Factory-assembled and wired, electric, [vertical] [horizontal] storage type, [[     ]-gal capacity, [     ]-kW input, recovery rate [     ]-gpm (L/s) with 100 deg F (37.7 deg C) temperature rise,] 150 psig (1035 kPa) maximum working pressure.

- <The following specifications represent two types of commercial water heaters; those that are mass produced and cataloged (Paragraphs B, C, and D), and those that are factory manufactured to specification (Paragraphs E, F, and G).  Select the paragraphs that are appropriate for the project. Copper-lined tanks should only be considered when water conditions dictate their use.>

        - [Glass-lined] [Copper-lined] welded steel tank; 4 inches (100 mm) diameter inspection port, thermally insulated with at least 2 inches (50mm) of glass fiber encased in corrosion-resistant steel jacket; baked-enamel finish.

        - Automatic immersion water thermostat; externally adjustable temperature range from 60 to 180 deg F (15.6 to 82,2 deg C), flanged or screw-in nichrome elements, high-temperature-limit thermostat.

        - Brass water connections and dip tube, drain valve, high-density magnesium anode, and ASME-rated temperature- and pressure-relief valve.

- <The lining materials are listed from most common to least common.  However, glass-lined tanks are only available in sizes specific to a manufacturer.>

        - Welded steel ASME-labeled pressure vessel; [glass] [phenolic] [cement] [copper] [nickel] lining, mounted on steel-channel base with lifting lugs, insulated with 2 inches (50mm) of glass fiber; enclosed with 16-gauge (1.52 mm) steel jacket; baked-enamel finish.

        - Ventilated control cabinet, factory-wired with solid-state progressive-sequencing step controller, fuses, magnetic contactors, control transformer, pilot lights that indicate main power and heating steps, control-circuit toggle switch, electronic low-water (probe-type) cut-off, high-temperature-limit thermostat, flush-mounted temperature and pressure gauges.

        - Flange-mounted immersion-heating electrical elements; individual elements sheathed with Incoloy corrosion-resistant metal alloy, rated less than 75 watts/sq in.

      - ACCEPTABLE MANUFACTURERS - PACKAGED WATER HEATING SYSTEM

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - PACKAGED WATER HEATING SYSTEM

- <References to direct vs. indirect boiler is relative to whether the service water passes directly through the boiler or through a heat exchanger.  The indirect water-heating boiler is coupled with the “steel boiler tubes and copper heat exchanger.”>

        - System of gas-fired [direct-heating boiler,] [indirect water-heating boiler,] circulating pump, controls, piping and valving as indicated, [storage tank [,] [all mounted on structural steel skid].

        - Gas-fired water-tube boiler, with [copper finned-tube heat exchanger,] [1-inch (25 mm) OD, 13-gauge (2.28 mm) steel boiler tubes and copper-tube heat exchanger with bronze heads,] steel jacket with glass-fiber insulation.

        - Boiler with gas burner, thermometer and pressure gauge, immersion thermostats for operating and high-limit protection, 100 percent safety shut-off electric gas valve with transformer, electronic safety pilot and pilot burner, gas-pressure regulator, manual gas shut-off, low-water cut off, ASME-rated temperature- and pressure-relief valve, [coil relief valve, automatic boiler fill and expansion tank,] draft inverter.

        - Boiler, with gross input [ ] Btu/hr, gross output [     ] Btu/hr, at sea level; [     ], [     ], or equal.

        - [Vertical] [Horizontal] storage tank [[ ]-inches long overall, [     ]-inches diameter] [nominal capacity [ ] gal], ASME-labeled for 150 psig (1035 kPa) working pressure, lined with [0.015-inch-thick epoxy] [     ] lining extended through flanges and couplings.

        - Supply tank with two welded tank saddles not less than 4 inches (100 mm) wide by 1/4 inches (6 mm) thick, mounted on 2-inch pipe stand with at least four crossbraced legs.  Provide sheet-Teflon isolation strip between tank and saddle.  Isolate tank from piping system with dielectric unions.  Factory-insulate tank with 3 inches of glass-fiber insulation with [steel] [aluminum] jacket.

        - Bronze, in-line circulation pump mounted [on boiler,] [between heater and storage tank,] controlled by tank-mounted immersion thermostat set at [140 deg F (60 deg C)] [     ].

          - Pump Capacity:  [     ] gpm (L/s) with [     ]-hp motor.

        - Provide three-way self-contained thermostatic valve, full-line size, bronze body 1/2 to 2-inch size (12 mm to 50 mm), iron body 2-1/2 inches (56 mm) and over, set at 140 deg F (60 deg C).

      - WATER HEATER ACCESSORIES

- 1.		Piping-Type Heat Traps:  Field-fabricated piping arrangement according to ASHRAE/IESNA 90.1-2004.

      - ACCEPTABLE MANUFACTURERS - HEAT EXCHANGERS

        - Piping-Type Heat Traps:  Field-fabricated piping arrangement according to ASHRAE/IESNA 90.1-2004.

      - ACCEPTABLE MANUFACTURERS - HEAT EXCHANGERS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - HEAT EXCHANGER CONSTRUCTION

        - Tubes:  U-tube type with at least 3/4 inches (20 mm) OD seamless-copper tubes suitable for 150 psig (1035 kPa) working pressure.

        - Heads; [Cast iron or steel,] [Brass,] with [steel] [brass] tube sheets, threaded or flanged for piping connections.

        - Water Chamber and Tube Bundle:  Removable for inspection and cleaning.

        - Coating:  Prime coat exterior.

        - Code:  ASME Code for pressure vessels for service pressures, ASME “U” symbol stamped on heat exchanger.

        - Shell and Tube Type:  Steel shell, with threaded or flanged piping connections and necessary tappings, steel saddle and attaching U-bolts, designed for heating fluid in shell and heated fluid in tubes.

        - Immersion Type:  Steel collar for welding to tank.

- <Select the following accessories for steam-to-water heat exchangers.>

        - Wells for temperature-regulator sensor [and high-limit sensor] at water outlet.

        - ASME-rated temperature- and pressure-relief valve on water outlet.

        - ASME-rated pressure-relief valves from tapping on heated-water side, set at 120-psig (828-kPa).

        - ASME-rated pressure-relief valve on steam inlet on downstream side of control valve.

        - Thermometers and pressure-gauge tappings in water inlet and outlet.

        - Vacuum breaker and pressure-gauge tapping with pigtail siphon in shell.

- <Select the following accessories for water-to-water heat exchangers.>

        - Wells for temperature-regulator sensor at heated-water outlet.

        - ASME-rated temperature- and pressure-relief valve on heated-water discharge.

        - ASME-rated pressure-relief valves from tapping on heated-water side, set at 120 psig.

        - ASME-rated pressure-relief valve on water inlet on downstream side of control valve.

        - Thermometers and pressure-gauge tappings on water inlets and outlets.

      - ACCEPTABLE MANUFACTURERS - DOMESTIC HOT WATER STORAGE TANKS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - DOMESTIC HOT WATER STORAGE TANKS

        - Tank:  Welded steel, ASME-labeled for working pressure of [125 psig (362.5 kPa), steel support saddles, tappings for accessories, threaded connections of stainless steel, access manhole.

        - Lining:  [Corrosion-resistant concrete approximately 3/4 inches (100 mm) thick] [0.015-inch epoxy] [    ], continued into flanged connections.

        - Openings:  Up to 3 inches (75 mm), copper-silicone threaded; over 4 inches (100 mm), flanged.

        - Accessories:  Tank drain, water inlet and outlet, thermometer range of 40 to 200 deg F (4.4 to 93.3 deg C), ASME pressure-relief valve suitable for maximum working pressure.

      - ACCEPTABLE MANUFACTURERS - UNDERGROUND FUEL STORAGE TANKS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - UNDERGROUND FUEL STORAGE TANKS

- <Tank construction is listed from most common to least common.>

        - UL listed and labeled, closed type, [reinforced glass-fiber polyester, able to store liquid with specific gravity of [1:1][ ] and temperatures up to 150 deg F (65.5 deg C)] [heavy-gauge welded steel, cleaned and coated with corrosion-resistant asphalt base paint] [heavy-gauge welded steel, epoxy coated], anchor straps and attachments, fittings, lifting lugs, and tappings for accessories.

        - Filler and vent outlets and fittings, galvanized vent includes “T” and elbow assembly with 1/4 inches (100 mm) square-mesh screen over inlet.

        - Provide 3 inches (75 mm) watertight brass cap and filler lock assembly.

        - Provide anti-siphon supply connection to tank bottom, 18 inches (457 mm) diameter manhole at top of tank, with cover, gasket, and sleeve.

      - ACCEPTABLE MANUFACTURERS - IN-LINE CIRCULATOR PUMPS

        - PACO.

        - ITT Bell & Gossett.

        - TACO.

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - IN-LINE CIRCULATOR PUMPS

        - Casing:  Bronze, rated for 125 psig (862.5 kPa) working pressure.

        - Impeller:  Bronze.

        - Shaft:  Alloy steel with integral thrust collar and two oil-lubricated bronze-sleeve bearings.

        - Seal:  Carbon rotating against a stationary ceramic seat.

        - Drive:  Flexible coupling.

        - Timers:  Electric time clock for control of hot-water circulation pump.

          - Type:  Programmable, [seven-day] <Insert other> clock with manual override on-off switch.

          - Enclosure:  Suitable for wall mounting.

          - Operation of Pump:  On or off.

          - Transformer:  Provide if required.

          - Power Requirement:  [24 V, ac] [120 V, ac] <Insert other>.

          - Programmable Sequence of Operation:  [Up to two on-off cycles each day for seven days] <Insert operational sequence>.

        - Time Delay Relay:  Control for hot-water storage tank circulation pump.

          - Type:  Adjustable time delay relay.

          - Range:  Up to five minutes.

          - Setting:  Five minutes.

          - Operation of Pump:  On or off.

          - Transformer:  Provide if required.

          - Power Requirement:  [24 V, ac] [120 V, ac] <Insert other>.

          - Programmable Sequence of Operation:  Limit pump operation to periods of burner operation plus maximum five minutes after the burner stops.

      - ACCEPTABLE MANUFACTURERS - PRESSURE BOOSTER SYSTEMS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - PRESSURE BOOSTER SYSTEMS

        - Packaged [two] [three] [four]-pump pressure-boosting system completely factory assembled, tested, and adjusted; shipped to site as integral unit; consisting of pumps, valves, and galvanized piping, with control panel assembled on fabricated steel base with structural-steel framework.

        - Locate controls and instruments in NEMA 1 general-purpose enclosure with main disconnect interlocked with door, fused circuit for each motor, magnetic starters with three overloads, control-circuit transformer with fuse protection, selector switch for each pump, low-limit pressure switch, low-pressure alarm light, running lights, current-sensing devices, minimum-run timers, manual alternation, and suction- and discharge-pressure gauges.

        - Lead pump shall operate continuously with lag [pump] [pumps] operating on system demand.  Should lead pump fail to operate, next pump in sequence shall start automatically.

        - Time-delay relay shall prevent lag [pump] [pumps] from short cycling on fluctuating demands.

        - Thermal bleed circuit with solenoid valve to prevent overheating during low demand.

        - Low-pressure control to stop pump operation if incoming water pressure drops to atmospheric.

        - Each pump with switch to permit manual or automatic operation.

- <If a system discharge-pressure-reducing valve is specified, then check valves on each pump discharge will be required.>

        - [Each pump outlet] [System discharge] combination pressure reducing and check valve to maintain constant system pressure.  Provide gate or butterfly valves on suction and discharge of each pump.  [Provide check valve on each pump discharge.]

        - Provide time clock for automatic day-night changeover.  During day cycle, system shall operate continuously with pressure to fixtures maintained by pressure-reducing valves.  During night cycle, [pump] [pumps] shall operate intermittently on pressure switch located near pressure tank operating pump for predetermined adjustable time period.

      - ACCEPTABLE MANUFACTURERS - SUMP PUMPS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - SUMP PUMPS

        - Type:  Vertical centrifugal, direct connected, [simplex] [duplex] arrangement.

        - Casing:  Cast-iron volute with radial clearance around impeller [with inlet strainer].

- <The inlet strainer, cast-iron construction, and closed impeller are only appropriate for storm water service.  Sanitary service does not require a strainer and must have an open impeller.  Cast iron vs. bronze impeller is generally a function of pump size and service.  Cast-iron impellers should be continuously submerged.>

        - Impeller:  [Cast iron;] [Bronze;] [open nonclog,] [closed,] keyed to [corrosion-resistant alloy steel] [stainless-steel] shaft.

        - Support:  Cast-iron pedestal motor support on steel floor plate with gas-tight gaskets.

        - Bearings:  [Forced-grease] [Oil]-lubricated bronze sleeve[s] spaced no more than 48-inches (1220 mm) apart and grease-lubricated ball-thrust at floor plate.

        - Drive:  Flexible coupling to vertical, solid-shaft ball-bearing electric motor.

        - Sump:  Steel cover plate [with steel-curb frame for grouting into concrete sump] [on steel-sump basin] with inspection opening and cover, and alarm fittings.

- <Select one of the two following paragraphs for the control desired.  If both are required for two different pumps, show types on pump schedule.  The controls listed are those most commonly applied to this type of pump.  However, controls as specified in Paragraphs 2.21.G and 2.21.H should be used in this type of installation.>

        - Controls (Simplex):  Float switch with float rod, stops, and corrosion-resistant float, and separate pressure-switch high-level alarm with transformer, alarm bell, and stand-pipe.

        - Controls (Duplex):  Float-operated mechanical alternator with float rod, stops, and corrosion-resistant float to alternate operation of pumps, cut-in second pump on rising level or lead-pump failure, [separate pressure-switch high-level alarm with transformer, alarm bell, and standpipe] [,] [and] [extra set of wired terminals for remote alarm circuit] [,] [and emergency float switch with float rod, stops, and corrosion-resistant float to operate both pumps on failure of alternator].

      - ACCEPTABLE MANUFACTURERS - SUBMERSIBLE PUMPS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Comply with Division 01 Section "General Requirements."

- <Edit the following descriptive specifications for conflicts with the manufacturer’s products specified above.>

      - SUBMERSIBLE PUMPS

        - Type:  Completely submersible vertical centrifugal.

- <The cast iron or bronze construction is generally a function of specific pump selection and pump service.  Cast iron should be continuously submerged.  Use the open impeller for sanitary sewage, and the closed for storm water.>

        - Casing:  [Cast-iron] [Bronze] pump body and oil-filled motor chamber.

        - Impeller:  [Cast iron;] [Bronze;] [open nonclog,] [closed,] [stainless steel] [corrosion-resistant-alloy steel] shaft.

        - Bearings:  Ball bearings.

        - Accessories:  Oil-resistant power cord with three-prong connector.

        - Servicing:  Slide-away coupling consisting of discharge elbow secure to sump floor, movable bracket, guide pipe system, lifting chain and chain hooks.

- <The following controls are generally appropriate only for single-phase motors up to 1 hp.>

        - Controls:  Integral [diaphragm] [mercury-switch]-type level controls [with separate liquid-level-control high-level alarm].

- <The following controls are for pump-motor installations larger than 1/2-hp and are suitable for three-phase electrical service.>

        - Motor-control panel containing across-the-line electric-motor starters with ambient-compensated quick-trip overloads in each phase with manual-trip button and reset button, circuit breaker, control transformer, electromechanical alternator, hand-off-automatic selector switches, pilot lights, high-water-alarm pilot light, reset button, and alarm horn.  Provide mercury-switch liquid-level controls, steel-shell switch encased in polyurethane foam with cast-iron weight for pump on (each pump), pump off (common), and alarm.

- EXECUTION

      - WATER HEATER INSTALLATION

        - Install water heaters in accordance with manufacturer’s instructions and to [AGA] [NSF] [NFPA] [UL] requirements.

        - Coordinate with plumbing piping and related [fuel piping] [gas venting] [electrical] work to achieve operating system.

        - Interlock pump with water heater burner and time delay relay.

      - HEAT EXCHANGER INSTALLATION

        - Install tanks in accordance with manufacturer’s instructions.

        - Install unit with clearance for tube-bundle removal without disturbing other installed equipment or piping.

        - Pipe relief valves and drains to nearest floor drain.  [Pitch shell for condensate drain to traps.]

        - Support unit [on pipe stand] [     ].

- <Use the following paragraphs for steam heat.>

        - Connect steam branch line from top of main.  Pipe in flexible manner, pitched with steam flow, with pipe union connections.  Provide steam-pressure gauge at exchanger inlet.

        - Provide steam traps and valves as indicated.  Pitch condensate return 1 inch in 20 feet (1:250) to return pump.

      - DOMESTIC HOT WATER STORAGE TANK INSTALLATION

        - Install tanks in accordance with manufacturer’s instructions.

        - B.	Provide [steel pipe] [     ] support for tanks, independent of building structural-framing members.

        - Clean and flush tank [prior to delivery to site] [after installation].  Seal until pipe connections are made.

      - UNDERGROUND TANK INSTALLATION

        - Install tanks in accordance with manufacturer’s instructions.

        - Clean and flush tank [prior to delivery to site] [after installation].  Seal until pipe connections are made.

        - Backfill steel tanks in accordance with NFPA 30 and 31.

        - Backfill glass-fiber tanks with [washed pea gravel] [granular fill specified in Division 31 Section "Backfill"].  Do not bed on timbers, beams, or cradles.

      - PUMP INSTALLATION

        - Install in accordance with manufacturer’s instructions.

        - Provide air cock and drain connection on horizontal pump casings.

        - Provide line-sized gate valve and strainer on suction and line-sized, soft-seated check valve and globe valve on discharge.

        - Decrease from line size with long-radius reducing elbows or reducers.  Support piping adjacent to pump such that no weight is carried on pump casings.  Provide supports under elbows on pump suction and discharge line sizes 4 inches and over.

        - Ensure that pumps operate at specified system fluid temperatures without vapor binding and cavitation, are nonoverloading in parallel or individual operation, and operate within 25 percent of midpoint of published maximum efficiency curve.

        - Align, and verify alignment of base-mounted pumps prior to start-up.

        - Ensure that shaft length allows sump pumps to be located at least 24 inches below lowest invert into sump pit and with at least 6-inches clearance from bottom of sump pit.

- END OF SECTION 223000