SECTION 224000 – PLUMBING FIXTURES

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Concrete reinforcement and accessories.

          - Water closets

          - Urinals

          - Lavatories

          - Sinks

          - Service sinks

          - Bathtubs

          - Showers

          - Drinking fountains

          - Electric water coolers

          - Wash fountains

          - Eyewash fountains

          - Emergency showers

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 07 Section "Joint Sealants" for sealing fixtures to walls and floors

          - Division 06 Section "Interior Architectural Woodwork for lavatory tops.

          - Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment".

          - Division 22 Section "Plumbing Specialties".

          - Division 22 Section "Plumbing Equipment".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 22 Section "Common Results for Plumbing" for codes and standards, and other general requirements.

        - American National Standards Institute (ANSI)

          - ANSI A112.6.1 	Supports for Off-the-Floor Plumbing Fixtures for Public Use

          - ANSI A112.18.1 	Finished and Rough Brass Plumbing Fixture Fittings

          - ANSI A112.19.1 	Enameled Cast Iron Plumbing Fixtures

          - ANSI A112.19.2 	Vitreous China Plumbing Fixtures

          - ANSI A112.19.3 	Stainless Steel Plumbing Fixtures (Designed for Residential Use)

          - ANSI A112.19.4 	Porcelain Enameled Formed Steel Plumbing Fixtures

          - ANSI A112.19.5 	Trim for Water-Closet Bowls, Tanks, and Urinals

          - ANSI Z124.1 	Gel-Coated Glass-Fiber Reinforced Polyester Resin Bathtub Units

          - ANSI Z124.2 	Gel-Coated Glass-Fiber Reinforced Polyester Resin Shower Receptor and Shower Stall Units

          - ANSI Z358.1 	Emergency Eye Wash and Shower Equipment

        - Air-Conditioning and Refrigeration Institute ARI 1010 Drinking Fountains and Self-Contained Mechanically Refrigerated Drinking Water Coolers

      - SUBMITTALS

        - Submit under provisions of Division 22 Section "Common Results for Plumbing - Review of Materials" and Division 01 Section "General Requirements."

        - LEED Submittals:

- 1.	Product Data for Credit WE [2] [3.1] [3.2] [2 and 3.1] [2, 3.1, and 3.2]:  Documentation indicating flow and water consumption requirements.

        - Submit Product Data for fixtures, including sizes, utility sizes, trim, and finishes.

        - Operation and Maintenance Data:

          - Submit operation and maintenance data under Division 01 Section "General Requirements – Operation and Maintenance Data"

          - Include fixture trim exploded view and replacement parts lists.

      - QUALITY ASSURANCE

        - Fixtures:  By same manufacturer throughout for each product specified.

        - Trim:  By same manufacturer throughout for each product specified.

      - WARRANTY

        - Provide [5] [     ]-year [manufacturer's] warranty.

        - Warranty:  Include coverage of [electric water-cooler compressor] [     ].

- PRODUCTS

- Water Efficient Products.  Where available, the contractor must purchase WaterSenseSM labeled products and other water efficient products and choose irrigation contractors who are certified through a WaterSenseSM labeled program.

<Provide a detailed list for each plumbing fixture and trim item required.  The "Acceptable Manufacturers" listings have been separated from the specific fixtures since manufacturers produce many types of fixtures.>

      - ACCEPTABLE MANUFACTURERS - FIXTURES

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions.

<Carefully edit any added descriptive specifications for any conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - FIXTURE TRIM

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions.

<Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - FLUSH VALVES

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions.

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - WATER CLOSET SEATS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions..

<Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - FIXTURE CARRIERS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions..

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - MIXING VALVES (THERMOSTATIC)

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions..

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

- ACCEPTABLE MANUFACTURERS - MIXING VALVES (PRESSURE BALANCED)

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions..

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - WASH FOUNTAINS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Section 1.09 D.2 Specified Items – Substitutes.

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - ELECTRIC WATER COOLERS

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions.

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

      - ACCEPTABLE MANUFACTURERS - EMERGENCY SAFETY EQUIPMENT

        - [     ].

        - [     ].

        - [     ].

        - Substitutions:  Under provisions of Division 01 Section "General Requirements" Paragraph 8.1.E.3 – Specified Items. Substitutions.

- <Carefully edit any added descriptive specifications for conflicts with the manufacturer's products specified above.>

- <Edit the following fixture requirements and select the products suitable for this project.  If more than one type is used, number the fixtures by inserting a drawing reference number after the generic name, e.g., Water Closet (WC-2).  Select applicable options.>

      - WATER CLOSET (WC-1)

- <The floor-mounted water closet is a siphon jet.  The wall-hung water closet may be either.>

        - Bowl:  NSI A112.19.2; [floor-mounted] [wall-hung] [siphon-jet] [blow-out] vitreous-china closet bowl, with elongated rim, 1-1/2 inch spud, china bolt caps; [     ], [     ], or equal.

- <Select one of the two following paragraphs.>

        - Flush Valve:  ANSI A112.18.1; exposed, chrome-plated, diaphragm type with oscillating handle, escutcheon, seat bumper, integral screwdriver stop and vacuum breaker; [     ], [     ], or equal.

        - Flush Valve:  ANSI A112.18.1; concealed, rough-brass, diaphragm type with exposed chrome plated [push button] [oscillating handle] and escutcheon, wheel handle stop and vacuum breaker; [     ], [     ], or equal.

        - Seat:  Solid [black] [white] plastic, open front, extended back, [self-sustaining hinge,] brass bolts, [without] cover; [     ], [     ], or equal.

- <Adjustable supports have a large adjustable face plate and are principally for horizontal piping connections.  Non adjustable supports have adjustable stands and are intended for vertical piping.>

        - Wall Mounted Carrier:  ANSI A112.6.1; [adjustable] [non adjustable] cast-iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers; [     ], [     ], or equal.

        - Flush Rate:  the flush rate shall be 1.6 gallons per flush or less.

      - WATER CLOSET (WC-2)

        - Bowl:  ANSI A112.19.2; wall hung, vitreous china, reverse trap, whirlpool action close-coupled closet combination with regular rim, insulated vitreous-china closet tank with fittings and lever flushing valve, chrome-plated bolt caps; [     ], [     ], or equal.

        - Seat:  Solid [black] [white] plastic, [open] [closed] front and cover, brass bolts; [     ], [     ], or equal.

- <Adjustable supports have a large adjustable face plate and are principally for horizontal piping connections.  Non adjustable supports have adjustable stands and are intended for vertical piping.>

        - Wall Mounted Carrier:  ANSI A112.6.1; [adjustable] [non adjustable] cast-iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers; [     ], [     ], or equal.

        - Flush Rate:  the flush rate shall be 1.6 gallons per flush or less.

      - WATER CLOSET (WC-3)

- <Use the 18-inch high unit in washrooms for the handicapped.>

        - A.	Bowl:  ANSI A112.19.2; floor mounted, siphon jet, vitreous china, [18-inches high] close-coupled closet combination with elongated rim, insulated vitreous-china closet tank with fittings and lever flushing valve, bolt caps; [     ], [     ], or equal.

        - B.	Seat:  Solid [black] [white] plastic, open front, extended back, less cover, complete with self-sustaining hinge; [     ], [     ], or equal.

        - Flush Rate:  the flush rate shall be 1.6 gallons per flush or less.

      - WATER CLOSET (WC-4)

        - Bowl:  ANSI A112.19.2; floor mounted, vitreous-china reverse trap, close-coupled closet combination with regular rim, insulated vitreous-china closet tank with fittings and lever flushing valve, bolt caps; [     ], [     ], or equal.

        - Seat:  Solid [black] [white] plastic with [open] [closed] front and cover, brass bolts; [     ], [     ], or equal.

        - Flush Rate:  the flush rate shall be 1.6 gallons per flush or less.

      - URINAL (UR-1)

- <The washout urinal has a stainless-steel strainer.  The blowout urinal has no strainer.>

        - Urinal:  ANSI A112.19.2; vitreous china, wall-hung [washout] [blowout] urinal with shields, integral trap, [removable stainless-steel strainer,] 3/4-inch [top] [back] spud, steel supporting hanger; [     ], [     ], or equal.

<Select one of the following three paragraphs.>

        - Flush Valve:  ANSI A112.18.1; exposed, chrome-plated, diaphragm type with [oscillating handle,] [push plate,] escutcheon, integral screwdriver stop [, vacuum breaker]; [     ], [     ], or equal.

        - Flush Valve; ANSI A112.18.1; concealed, rough-brass, diaphragm type with exposed chrome-plated [push button] [oscillating handle] and escutcheon, wheel handle stop and vacuum breaker; [     ], [     ], or equal.

### <The metering valve may not be suitable for water qualities.>

        - Metering Valve:  ANSI A112.18.1; exposed, chrome-plated, porous-felt type for 1/2-inch supply with [oscillating handle,] [push button,] screwdriver stop [and vacuum breaker]; [     ], [     ], or equal.

        - Wall Mounted Carrier:  ANSI A112.6.1; cast-iron and steel frame with tubular legs, lugs for floor and wall attachment, threaded fixture studs for fixture hanger, bearing studs; [     ], [     ], or equal.

        - Flush Rate:  Pint unit, the flush rate shall be 1/8 gallons per flush or less.

        - Flushometers:  Flushometer for [urinal] [water-closet]-type fixture.  Include brass body with corrosion-resistant internal components,[ non-hold-open feature,] control stop with check valve, vacuum breaker, copper or brass tubing, and polished chrome-plated finish on exposed parts.

          - Consumption:  [0.5 gal./flush] [1.0 gal./flush] .

      - URINAL (UR-2)

        - Urinal:  ANSI A112.19.2; vitreous-china, slope-front stall urinal with integral flushing rim, removable stainless-steel strainer 3/4-inch top spud; [     ], [     ], or equal.

- <Select one of the following three paragraphs.>

        - Flush Valve:  ANSI A112.18.1; exposed, chrome-plated, diaphragm type with [oscillating handle,] [push plate,] escutcheon, integral screwdriver stop [and vacuum breaker]; [     ], [     ], or equal.

        - Flush Valve:  ANSI A112.18.1; concealed, rough-brass, diaphragm type with exposed chrome plated [push button] [oscillating handle] and escutcheon, wheel handle stop and vacuum breaker; [     ], [     ], or equal.

        - Tank:  ANSI A112.19.5; vitreous-china insulated tank with concealed cover, [bottom] [overrim] supply, siphon valve; [     ], [     ], or equal.

        - Flush Rate:  Pint unit, the flush rate shall be 1/8 gallons per flush or less.

        - Flushometers:  As Section 2.14 G above.

      - LAVATORY (L-1)

        - Basin:  [ANSI A112.19.2; vitreous-china] [ANSI A112.19.1; porcelain-enameled, cast-iron] wall-hung lavatory [      ¥      ] inch minimum, with 4-inch high back, drillings on [4] [8]-inch centers, rectangular basin with splash lip, front overflow, and soap depression; [     ], [     ], or equal.

- <Select one of the two following paragraphs.  The combination supply fitting has the pop-up waste.  Use the other two options for standard fittings.>

        - Trim:  ANSI A112.18.1; chrome-plated [combination] supply fitting with [pop-up waste,] [chain and plug,] [open-grid strainer,] water economy aerator, [indexed handles,] [single-lever handle,] chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; chrome-plated metered mixing faucet with [aerator] [spray] and coverplate, open-grid strainer, chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Wall Mounted Carrier:  ANSI A112.6.1; cast-iron and steel frame with tubular legs, lugs for floor and wall attachment, [threaded studs for fixture hanger,] [concealed arm supports,] bearing plate and studs; [     ], [     ], or equal.

        - Faucet:  [Single-control mixing] [Single-control nonmixing] [Two-handle mixing] <Insert type> valve.  Include hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture holes; coordinate outlet with spout and fixture receptor.

- 1.	Maximum Flow Rate:  [0.5 gpm] [2.2 gpm] [2.5 gpm] <Insert value>.

- 2.		Maximum Flow:  [0.25 gal.] <Insert amount>.

      - LAVATORY (L-2)

        - Lavatory:  [ANSI A112.19.4; porcelain-on-steel] [ANSI A112.19.2; vitreous-china] self-rimming countertop lavatory, [     ¥     ] inches with drillings on [4] [8]-inch centers, front overflow, [soap depression,] seal of putty, caulking, or concealed vinyl gasket; [     ], [     ], or equal.

- <Select one of the two following paragraphs.  The combination supply fitting has the pop-up waste.  Use the other two options for standard fittings.>

        - Trim:  ANSI A112.18.1; chrome-plated [combination] supply fitting with [pop-up waste,] [chain and plug,] [open-grid strainer,] water-economy aerator, [indexed handles;] [single-lever handle,] chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; chrome-plated metered mixing faucet with [aerator] [spray] and coverplate, open-grid strainer, chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Faucet:  As Section 2.16 E above.

      - SINK (S-1)

- <Types 302 and 304 stainless steel are suitable for general use.  Use Type 316, in combination with stainless-steel drain, for use where chemicals will be encountered.>

        - Bowl:  ANSI A112.19.3; single compartment [     ¥     ¥     ] inch outside dimensions, [20] [     ]-gauge, Type [302] [304] [316] stainless steel, self-rimming with undercoating, 3-1/2 inch crumb cup and [chromed-brass] [stainless-steel] drain, ledge back drilled for trim; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; chrome-plated brass supply with swing spout, water-economy aerator, [indexed lever handles] [single lever handle] [and retractable spray]; chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Faucets:  [Kitchen faucet with spray, three-hole fixture] [Kitchen faucet with spray, four-hole fixture] [Kitchen faucet without spray] [Laundry tray faucet] [Service sink faucet with stops in shanks, vacuum breaker, hose-thread outlet, and pail hook] [Bar sink faucet] <Insert type>.  Include hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture holes; coordinate outlet with spout and fixture receptor.

- 1.		Maximum Flow Rate:  [2.5 gpm] <Insert value>, unless otherwise indicated.

      - SINK (S-2)

- <Types 302 and 304 stainless steel are suitable for general use.  Use Type 316, in combination with stainless-steel drain, for use where chemicals will be encountered.>

        - Bowl:  ANSI A112.19.3; double compartment [     ¥     ¥     ] inch outside dimensions, [[20] [     ]-gauge] [[0.9] [     ]-inch thick] Type [302] [304] [316] stainless steel, self-rimming with undercoating, 3-1/2 inch crumb cups, and [chromed-brass] [stainless-steel] drain, ledge back drilled for trim; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; chrome-plated brass supply with swing spout, water-economy aerator, [indexed lever handles] [single-lever handle] [and retractable spray]; chrome-plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Faucets:  As Section 2.18 C above.

      - SINK (S-3)

        - Bowl:  [ANSI A112.19.4; steel,] [ANSI A112.19.1; cast iron,] porcelain-enameled [single] [double] compartment, [     ¥     ¥     ] inch outside dimensions, self-rimming and undercoated, with 3-1/2 inch diameter crumb cup and [chromed-brass] [stainless-steel] drain, ledge back drilled for trim; [     ], [     ], or equal.

        - Trim:  ANSI 112.18.1; chrome-plated brass supply with swing spout, water economy aerator, [indexed lever handles] [single lever handle] [and retractable spray], chrome plated 17-gauge brass P-trap [with clean-out plug] and arm with escutcheon; [     ], [     ], or equal.

        - Faucets:  As Section 2.18 C above.

      - BATHTUB [AND SHOWER] (B-1)

        - Bathtub:  ANSI A112.19.4; porcelain-on-steel bathtub [with slip resistant surface,] contoured front apron, [60] [     ] inches long; [     ], [     ], or equal.

        - Select one of the following three paragraphs.

        - Trim:  ANSI A112.18.1; concealed overrim supply with spout and indexed handles, lever-operated pop-up waste and overflow; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; concealed shower and overrim supply with diverter spout, indexed handles, bent shower arm with [flow control and] [adjustable-spray] ball-joint showerhead and escutcheon, lever-operated pop-up waste and overflow; [     ], [     ], or equal.

- <The pressure-balanced valve is most suitable for single shower installations.  Thermostatic mixing valves require flow to maintain good control.>

        - Trim:  ANSI A112.18.1; concealed shower and overrim supply with diverter spout, [pressure-balanced] [thermostatic] mixing valve, bent shower arm with [flow control and] [adjustable spray] ball-joint showerhead and escutcheon, lever-operated pop-up waste and overflow; [     ], [     ], or equal.

        - Showerhead:  Based on ASME test procedure A772.78M-1994, the flow rate shall be 2.2 gallons per minute or less at an inlet water pressure of 80 psi.

        - Faucets:  Single-handle [pressure-balance] [thermostatic] [thermostatic/pressure-balance] <Insert type> valve for bathtub and for shower.  Include hot- and cold-water indicators; check stops; tub spout; and shower head, arm, and flange.  Coordinate faucet inlets with supplies; coordinate outlet with diverter valve.

          - Maximum Flow Rate:  [2.2 gpm] <Insert value>, unless otherwise indicated.

- 2.		Shower-Arm Flow-Control Fitting:  [Not required] [1.5 gpm] [2.0 gpm].

      - BATHTUB [AND SHOWER] (B-2)

- <Specify color if applicable.>

        - Bathtub:  ANSI Z124.1; molded glass-fiber-reinforced polyester, [with slip-resistant bottom surface,] contoured shape, [60] [     ] inches long ¥ [30] [     ] inches wide; [     ], [     ], or equal.

- <Select one of the following three paragraphs.>

        - Trim:  ANSI A112.18.1; concealed overrim supply with spout and indexed handles, lever-operated pop-up waste and overflow; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; concealed shower and overrim supply with diverter spout, indexed handles, bent shower arm with [flow control and] [adjustable spray] ball-joint showerhead and escutcheon, lever-operated pop-up waste and overflow; [     ], [     ], or equal.

- <The pressure-balanced valve is most suitable for single shower installations.  Thermostatic mixing valves require flow to maintain good control.>

        - Trim:  ANSI A112.18.1; concealed shower and overrim supply with diverter spout, [pressure-balanced] [thermostatic] mixing valve, bent shower arm with [flow control and] [adjustable spray] ball-joint showerhead and escutcheon, lever operated pop-up waste and overflow; [     ], [     ], or equal.

        - Showerhead:  Based on ASME test procedure A772.78M-1994, the flow rate shall be 2.2 gallons per minute or less at an inlet water pressure of 80 psi.

        - Faucets:  As Section 2.21 G above.

      - SHOWER (SH-1)

- <The integral seat is available only with reinforced glass-fiber units.  The stone-texture receptor is available only with enameled-steel units.>

        - Cabinet:  [ANSI A112.19.4; porcelain-enameled steel] [ANSI Z124.2 reinforced glass fiber], [32 ¥ 32 ¥ 75] [     ¥     ¥     ]-inch high, with [stone-texture] receptor, soap dish, [integral seat,] removable chrome-plated strainer, tailpieces; [     ], [     ], or equal.

- <Select one of the following two paragraphs.>

        - Trim:  ANSI A112.18.1; concealed shower supply with indexed handles, bent shower arm with [flow control and] [adjustable spray] ball-joint shower head and escutcheon; [     ], [     ], or equal.

<The pressure-balanced valve is most suitable for single shower installations.  Thermostatic mixing valves require flow to maintain good control.>

        - Trim:  ANSI A112.18.1; concealed shower supply with [pressure-balanced] [thermostatic] mixing valves, bent shower arm with [flow control and] [adjustable spray] ball-joint shower head and escutcheon; [     ].

        - Showerhead:  Based on ASME test procedure A772.78M-1994, the flow rate shall be 2.2 gallons per minute or less at an inlet water pressure of 80 psi.

        - Faucets:  Single-handle [pressure-balance] [thermostatic] [thermostatic and pressure-balance] valve.  Include hot- and cold-water indicators; check stops; and shower head, arm, and flange.  Coordinate faucet inlets with supplies and outlet with diverter valve.

          - Maximum Flow Rate:  [2.2 gpm] <Insert value>, unless otherwise indicated.

- 2.		Shower-Arm Flow-Control Fitting:  [Not required] [1.5 gpm] [2.0 gpm].

      - SHOWER (SH-2)

        - A.	Shower Head:  ANSI A112.18.1:  chrome-plated vandal-proof institutional head with integral wall bracket, built-in 2-1/2 gal/min. flow control; [     ], [     ], or equal.

        - <Select one of the following three paragraphs; use Paragraph B or C only when tempered water is provided.>

        - Trim:  ANSI A112.18.1; concealed straight-way pattern valve with indexed cross handle.

        - Trim:  ANSI A112.18.1; concealed rough-brass metering valve with closed fluid metering system adjustable from 5 to 120 seconds, chrome-plated push button and escutcheon, wheel handle stop; [     ], [     ], or equal.

- <The pressure-balanced valve is most suitable for single shower installations.  Thermostatic mixing valves require flow to maintain good control.>

        - Trim:  ANSI A112.18.1; concealed shower supply with [pressure-balanced [thermostatic] mixing valves, bent shower arm with [flow] control and] [adjustable spray] ball-joint shower head and escutcheon; [     ], [     ], or equal.

        - Showerhead:  Based on ASME test procedure A772.78M-1994, the flow rate shall be 2.2 gallons per minute or less at an inlet water pressure of 80 psi.

        - Faucets:  As Section 2.23 E above.

      - DRINKING FOUNTAIN (DF)

- <Select one of the following paragraphs.>

        - Fountain:  Molded [white] [     ] reinforced glass fiber with underside vandal-proof cowling, hooded elevated anti-squirt bubbler with stream guard, automatic stream regulator, [cross] [lever] handle, mounting bracket, screwdriver stop; [     ], [     ], or equal.

        - Fountain:  [White] [     ] [reinforced glass fiber,] [vitreous china,] [semi-recessed,] [fully recessed,] with elevated anti-squirt bubbler with stream guard, automatic stream regulator, [cross] [lever] handle, access cover plate, mounting bracket, screwdriver stop; [     ], [     ], or equal.

      - ELECTRIC WATER COOLER (EWC)

        - Fountain:  ARI 1010; [surface-mounted] [semi-recessed] [recessed] [handicapped] electric water cooler with stainless steel top, [vinyl-on-steel] [stainless-steel] [     ] body, elevated anti-squirt bubbler with stream guard, automatic stream regulator, mounting bracket, refrigerated with integral air-cooled condenser; capacity of [     ] gal/min of 50 F water with inlet at 80 F and room temperature of 90 F, [     ]-hp compressor; [     ].

      - 2.28	WASH FOUNTAINS (WF)

        - Bowl:  Semi-circular, 36-inch diameter, [precast stone;] [enameled steel;] [stainless steel]; [     ], [     ], or equal.

        - Accessories:  Foot-controlled self-closing valve, spray head, liquid-soap dispenser, manual mixing valve, supporting tube, spud and strainer, operating mechanism, foot levers and rail, combination stop, strainer and check valves.

      - SERVICE SINK (SS-1)

        - Bowl:  ANSI A112.19.1; 22 ¥ 18 ¥ 12-inch deep, porcelain-enameled (inside only) cast-iron roll-rim sink, with 12-inch high back, concealed hanger, chrome-plated strainer, cast-iron P-trap with adjustable floor flange; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1 exposed wall-type supply with [cross] [lever] handles, spout wall brace, vacuum breaker, hose-end spout, strainers, eccentric adjustable inlets, integral screwdriver stops with covering caps and adjustable threaded wall flanges; 5 feet of 1/2-inch diameter plain-end reinforced [plastic] [rubber] hose, hose clamp, mop hanger; [     ], [     ], or equal.

      - SERVICE SINK ((SS-2)

        - Bowl:  [36] [24] ¥ 24 ¥ 10-inch high [white] [     ] molded stone, floor mounted, with 1-inch wide shoulders, stainless-steel strainer; [     ], [     ], or equal.

        - Trim:  ANSI A112.18.1; exposed-wall-type supply with [cross] [lever] handles, spout wall brace, vacuum breaker, hose-end spout, strainers, eccentric adjustable inlets, integral screwdriver stops with covering caps and adjustable threaded wall flanges; 5 feet of 1/2-inch diameter plain-end reinforced [plastic] [rubber] hose, hose clamp, mop hanger; [     ], [     ], or equal.

      - EMERGENCY EYE [AND FACE] WASH (EW-1)

        - ANSI Z358.1; [wall-mounted,] [free-standing,] self-cleaning, non clogging eye [and face] wash with quick-opening, full-flow valves, [stainless-steel] [ABS] eye [and face] wash receptor, twin eye-wash heads [and face-spray ring,] [stainless-steel dust cover,] [copper-alloy] [PVC] control valve and fittings; [     ], [     ], or equal.

      - EMERGENCY SHOWER (EW-2)

        - ANSI Z358.1; [wall-mounted,] [free-standing,] self-cleaning, non clogging 8-inch diameter [stainless steel] [copper alloy] [plastic] deluge shower head with elbow, 1-inch full-flow valve with pull chain and 8-inch diameter ring, 1-inch interconnecting fittings; [     ], [     ], or equal.

- EXECUTION

      - INSPECTION

        - Review architectural woodwork Shop Drawings.  Confirm location and size of fixtures and openings before rough-in and installation.

        - Verify that adjacent construction is ready to receive rough-in work of this section.

      - INSTALLATION

        - Install each fixture with a trap that is easily removable for servicing and cleaning.

        - Provide chrome-plated rigid or flexible supplies to fixtures with [loose key] [screwdriver] [     ] stops, reducers, and escutcheons.

        - Install components level and plumb

        - Install and secure fixtures in place with [wall supports] [wall carriers] and bolts.

        - Seal fixtures to wall and floor surfaces with sealant as specified in Division 07 Section "Joint Sealants", color to match fixture.

        - Install fixtures to the following mounting heights above finished floor:

- <Edit to suit project requirements.  Use this table only when fixture mounting heights are different or adjustable.  Shower-head heights listed are manufacturer's recommendations.>

| ### Water Closet: |  |  |
| --- | --- | --- |
| ### Standard | ### 15 inches (381 mm) to top of bowl rim |  |
| ### Handicapped | ### 18 inches (457 mm) to top of seat |  |
| ### Urinal: |  |  |
| ### Standard | ### 22 inches (559 mm) to top of bowl rim |  |
| ### Handicapped | ### 19 inches (483 mm) to top of bowl rim |  |
| ### Lavatory: |  |  |
| ### Standard | ### 31 inches (787 mm) to top of basin rim |  |
| ### Handicapped | ### 32 inches (813 mm) to top of basin rim |  |
| ### Drinking Fountain: |  |  |
| ### Standard | ### [30] [40] inches ([762] [1016] mm) to top of basin rim |  |
| ### Handicapped | ### 36 inches (914 mm) to top of basin rim |  |
| ### Water Closet Flush Valves: |  |  |
| ### Standard | ### 11 inches (280 mm) minimum above bowl rim |  |
| ### Recessed | ### 10 inches (254 mm) minimum above bowl rim |  |
| ### Shower Heads: |  |  |
| ### Adult [male] | ### 69.5 inches (1765 mm) to bottom of head |  |
| ### Adult [female] | ### 64.5 inches (1638 mm) to bottom of head |  |
| ### Child | ### 58.5 inches (1486 mm) to bottom of head |  |
| ### Emergency Eye [And Face] Wash: |  |  |
| ### Standard | ### 38 inches (965 mm) to receptor rim |  |
| ### Emergency Shower: |  |  |
| ### Standard | ### 84 inches (2134 mm) to bottom of head |  |

      - ADJUSTING AND CLEANING

        - Adjust stops or valves for intended water-flow rate to fixtures without splashing, noise, or overflow.

        - At completion, clean plumbing fixtures and equipment.

        - Solidly attach water closets to floor with lag screws.  Lead flashing is not intended hold fixture in place.

      - FIXTURE ROUGH-IN SCHEDULE

        - Rough-in fixture piping connections in accordance with following table of minimum sizes for particular fixtures.

<Edit to suit project requirements.  Expand to include other fixtures.  Use to avoid indicating the size of all runout piping on Drawings.>

|  | Hot Water | Cold Water | Waste | Vent |
| --- | --- | --- | --- | --- |
| Lavatory | 1/2-inch | 1/2-inch | 1-1/2 inch | 1-1/4 inch |
| Service Sink | 1/2-inch | 1/2-inch | 2 inch | 1-1/2 inch |
| Sink | 1/2-inch | 1/2-inch | 1-1/2 inch | 1-1/4 inch |
| Drinking Fountain | — | 1/2-inch | 1-1/4 inch | 1-1/4 inch |
| Water Closet (Flush Valve) | — | 1 inch | 4 inch | 2 inch |
| Water Closet (Tank Type) | — | 1/2-inch | 4 inch | 2 inch |
| Urinal (Flush Valve) | — | 3/4-inch | 2 inch | 1-1/2 inch |
| Urinal (Tank Type) | — | 1/2-inch | 2 inch | 1-1/2 inch |

END OF SECTION 224000