SECTION 260533 – ELECTRICAL CONDUIT

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Rigid metal conduit and fittings.

          - Intermediate Metal Conduit and fittings

          - Electrical metallic tubing and fittings.

          - Flexible metal conduit and fittings.

          - Liquid tight flexible metal conduit and fittings.

          - Non-metallic conduit and fittings.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 01, Section 013523.11, Lateral Force Procedures.

          - Division 03, Section 033000, Cast-in-Place Concrete.

          - Division 07, Section 078413, Penetration Firestopping.

          - Division 26, Section 260500, Common Work Results for Electrical.

          - Division 26, Section 260501, Inspections and Testing for Electrical Work.

          - Division 26, Section 260526, Secondary Grounding for Electrical Systems.

          - Division 26, Section 260533.13, Boxes for Electrical Systems.

          - Division 26, Section 260536, Cable Trays for Electrical Systems.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated.  Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01, Section 010000, General Requirements, for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - ANSI – American National Standards Institute:

          - ANSI C80.1 and UL 6 	Rigid Steel Conduit, Zinc Coated (RMC).

          - ANSI C80.3 and UL 797 	Electrical Metallic Tubing, Zinc Coated (EMT).

          - ANSI C80.5 and UL 6A 	Rigid Aluminum Conduit (ARC).

          - ANSI C80.6 and UL 1242 	Intermediate Metal Conduit, Zinc Coated (IMC).

        - LBNL Construction Details and Design Guidelines (CDDG), Vol. 3 – Construction Details, Part VI – Electrical Details.

        - NEMA – National Electrical Manufacturers Association:

          - NEMA FB 1 	Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, EMT and Cables.

          - NEMA RN 1 and UL 6 	Polyvinyl Chloride (PVC) Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit.

          - NEMA TC 2 and UL 651	Electrical Rigid Polyvinyl Chloride (PVC) Conduit.

          - NEMA TC3 	PVC Fittings for use with Rigid PVC Conduit and Tubing.

        - WW-C-566 - Flexible Metal Conduit.

      - SUBMITTALS

        - Submit under provisions of Division 01, Section 010000, General Requirements, “Submittals”; Division 01, Section 013500, Special Procedures, “Drawings and Specifications”; Division 26, Section 260500, Common Work Results for Electrical, “Submittals"; and as required by other sections of the Specifications.

        - Shop Drawings:  The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01, Section 010000, General Requirements, “Submittals”, and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the LBNL Facilities Division Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Submit shop drawings and product data for conduit, conduit fittings, and associated materials.  Clearly identify the specific product and material intended to be used.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc. or by a nationally recognized testing laboratory (NRTL) in accordance with Division 26, Section 260500, Common Work Results for Electrical.

        - Materials shall be new and within one year of the manufacture complying with all the latest codes and standards.  No used or refurbished materials shall be furnished and installed under this project.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver materials to site in unopened cartons or bundles as appropriate, clearly identified with manufacturer's name, Underwriter's or other approved label, grade or identifying number.

        - Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect equipment and material from dirt, water, construction debris, and traffic.

- PRODUCTS

      - RIGID METAL CONDUITS (RMC and IMC) AND FITTINGS

        - Rigid Steel Conduit:  ANSI C80.1 and UL 6, RMC  full-weight pipe, hot-dip galvanized with threaded ends, top coated outside to protect against white rust, a standard fully threaded coupling on one end, plastic cap on both ends; Republic Conduit, Allied Tube and Conduit, Wheatland Tube Company or equal.

        - Rigid Aluminum Conduit:  ANSI C80.5 and UL 6A; ARC, full-weight pipe, built to the same standards as rigid steel conduit with threaded ends, a standard fully threaded coupling on one end, plastic caps on both ends; Republic Conduit, Allied Tube and Conduit, Wheatland Tube Company or equal.  Only aluminum fittings shall be used with aluminum conduit.

        - Intermediate Metal Conduit:  ANSI C80.6 and UL 1242, IMC, high strength steel metal pipe, hot dip galvanized with threaded ends, top coated to avoid white rust, a standard fully threaded coupling on one end, plastic caps on both ends, interior coated with highly corrosion resistant lubricating finish for easier wire pulling; Republic Conduit, Allied Tube and Conduit, Wheatland Tube Company or equal.

        - PVC Externally Coated Conduit:  NEMA RN 1 and UL 6; rigid steel conduit with external 0.040-inch exterior gray PVC coating and internal galvanized surface, a fully threaded, PVC coated coupling on one end, plastic cap on both ends; Perma-Cote, Kor-Kap, Plasti-bond, OCal or equal.

        - Fittings and Conduit Bodies:  NEMA FB 1; threaded type, fitting material shall match conduit material (i.e., steel with steel, aluminum with aluminum), with a gasketed cover; O-Z Gedney Form 7 or equal.  Threadless fittings are not acceptable for RMC and IMC.

        - Watertight Expansion and Deflection Fittings:  Provide fittings at each building expansion joint for straight conduit run longer than 200 feet, weatherproof for outdoor installation with bonding jumper across each expansion fitting for ground continuity, Deflection fittings capable of accommodating not less than 3/4-inch displacement from normal condition in any direction including longitudinal (conduit centerline) direction; O-Z Gedney Type AX, DX, AXDX, EX, EXPB, PW, PBW, Crouse Hinds, or equal.

        - Insulated Grounding Type Bonding Bushings:  In threaded metal conduits for terminations to motor control center, switchgear, panels, switchboard, power circuit pull boxes, junction and termination boxes; O-Z Gedney Type BLG for RMC and IMC, Type ABLG for ARC, Thomas and Betts or equal.

        - Insulating Bushings:  for conduit terminations to lighting fixtures, pull boxes and junction boxes containing control wiring; O-Z Gedney Type A, Thomas and Betts or equal.

        - Flashing and Counter flashing:  Threaded cast iron flash and counter-flash units with bushings if required to accommodate conduit size, Semco No. 1100-2 Series, J.R. Smith No. 1750 Series, or equal.

        - Corrosion Protection:  When ferrous conduit is threaded in the field, the threads shall be coated with an approved electrically conductive, corrosion resistant compound intended for the purpose.  No other tapes, greases or compounds are permitted.

      - RIGID NON-METALLIC CONDUIT AND FITTINGS

        - Conduit:  Materials those are resistant to moisture and corrosive agents; sufficiently strong to withstand abuse normal to its installation conditions; rigid PVC or equal.

        - Fittings and Conduit Bodies:  NEMA FB 1.

      - ELECTRICAL METALLIC TUBING (EMT) AND FITTINGS

        - EMT:  ANSI C80.3 and UL 797; lightweight thinwall conduit, rigid steel, electro-galvanized and enameled on the inside; "X-Duct Jr.," "GE EMT," "Electrounit," or equal.

        - Fittings and Conduit Bodies:  NEMA FB 1; steel, compression type, rated for the installation conditions.  Set-screw or crimp-on type fittings are not acceptable.  Aluminum fittings or conduit bodies are not allowed with EMT.

        - EMT Connectors:  Insulated throat type, Thomas and Betts, Appleton Electric Co. or equal, rated for the installation conditions.

      - FLEXIBLE METAL CONDUIT (FMC) AND FITTINGS

        - Conduit:  WW-C-566; steel; liquid-tight, interlocking single-strip type with overall molded jacket to exclude moisture; "Sealtite," Condu-Flex, or equal.

        - Fittings and Conduit Bodies:  NEMA FB 1; steel; clamp or screw-in type.

        - Flexible Conduit Connectors:  Thomas and Betts, Appleton Electric Co. or equal, galvanized steel with integral insulated throat.

      - LIQUIDTIGHT FLEXIBLE CONDUIT AND FITTINGS

        - Conduit:  Flexible metal conduit with PVC jacket.

        - Fittings and Conduit Bodies:  NEMA FB 1.

        - Flexible Conduit Connectors:  Thomas and Betts, Appleton Electric Co. or equal, galvanized steel with integral insulated throat.

      - PLASTIC CONDUIT AND FITTINGS

        - Conduit:  NEMA TC 2

        - Fittings and Conduit Bodies:  NEMA TC 3.

      - SUPPORTS AND ATTACHMENTS

        - Conduit Clamps, Straps, and Supports:  Steel or malleable iron.  Devices or hardware using spring tension or friction for securing or supporting are not permitted.

        - Concrete Drilled Anchors:  Refer to Division 03, Section 031500, Concrete Accessories, for approved anchors.

        - Self-Drilling and Self-Tapping Bolts:  Atlas Corp. "Teks 2", or equal.

        - Sheetmetal Screws:  Parker-Kalon, American or equal, self-tapping, hardened steel, cadmium plated, binding head or countersunk flat head to suit application.

        - Hanger Rods:  1/4 inch minimum, hot dip galvanized Unistrut Corp., Super Strut Corp., or equal, applied as shown.  Use channel nuts, hex nuts, saddle type and flat washers and similar accessory items, each best suited to specific application:

          - Channel section, 12-gage (2.75 mm), 1-5/8 x 2-7/16 inches (9.53 by 39.7 mm):  P5500.

          - Studs, nuts and similar items:  of sizes and types noted and compatible with channel section to which applied.

          - Flat plate, angle, shaped and special fittings and beam clamps, of types noted and compatible with channel section to which applied.

          - Conduit straps:  P2580-10 to P2553-40, two holes type.

          - Conduit straps:  Appleton, Steel City, or equal, one-hole, sheet steel, for 1/2 and 3/4-inch conduits only.

          - "U" bolts:  Schedule 40 pipe sizes with threaded legs and nuts.

          - Universal pipe clamps, 1/2 to 2 inches (13 to 50 mm) conduits:  P2911 to P2917.

          - I.P.S. type pipe hangers as shown.

      - WARNING TAPE

        - Material:  Six-inch wide, 4-mil thick film, of inert material such as polyethylene plastic; impervious to acids, alkalis, and other soil components; and supplied in continuous roll.

        - Color/Message:  Bright yellow, red, or orange, electrically-detectable, film, with two-line message in permanent one-inch bold letters, one side only.  The following message to be repeated continuously the full length of the tape:

"CAUTION  CAUTION  CAUTION"

"[HIGH-VOLTAGE] ELECTRIC LINE BELOW"

        - Acceptable Manufacturers:

          - Thomas & Betts, Carlton Industries, Inc., Seton Nameplate Co., D & G Sign and Label Co., or equal.

          - Substitutions:  Comply with Division 01, Section 010000, General Requirements, “Materials And Equipment”.

- EXECUTION

      - CONDUIT INSTALLATION SCHEDULE

| Location or Use | Conduits Permitted |
| --- | --- |
| Underground Electrical Utility. | Reinforced Concrete encased PVC conduit with wrapped or PVC-coated RSG for bends, 90 degree stub ups and risers. |
| Under building slab. | Wrapped or PVC-coated RSG conduit. |
| In building concrete slab with LBNL approval. | Wrapped or PVC-coated RSG conduit. |
| Exposed outdoors, indoor damp or wet locations and in hazardous locations. | RSG, liquid-tight flexible conduit (refer to length restrictions and limited applications in this Section), IMC with LBNL approval. |
| Outdoor and indoor stub-ups to 5 feet (1.5 m) riser above finished grade or floor. | RSG, IMC with LBNL approval. |
| Exposed indoors above 5 feet (1.5 m) or in furred walls or ceiling space. | RSC, IMC or ARC if 3 inch (75 mm) or larger; EMT, galvanized flexible conduit (refer to length restrictions and limited applications in this Section). |
| Exposed indoors above suspended ceiling. | RSC, IMC or ARC if 3 inch (75 mm) or larger; EMT, galvanized flexible conduit (refer to length restrictions and limited applications in this Section). |
| Exposed indoors below 5 feet in labs, high-bays, electrical rooms, mechanical rooms, elevator rooms and shafts, hall ways, and all other areas not specified in this Section. | RSG, galvanized flexible conduit (refer to length restrictions and limited applications in this Section). |
| Exposed indoors (dry locations only) below 5 feet (1.5 m) in office areas not subject to physical damage. | EMT |

        - Install wiring and cables in conduit or other wiring raceway systems covered in this Division.  Provide separate raceway systems for each of the following wiring categories:

          - 480Y/277 Volt normal power.

          - 480Y/277 Volt emergency power.

          - 208Y/120 Volt normal power.

          - 208Y/120 Volt emergency power.

          - Variable Frequency Drives (VFD):  line, load, and control wiring in separate conduits.

          - Fire alarm.

          - EMCS/FMCS and other class 2 & 3 circuits.

          - SCADA System.

          - Intercommunication system.

      - CONDUIT SIZE, ARRANGEMENT, AND SUPPORT

        - Minimum conduit size:

          - The minimum conduit size shall be 3/4 inch (18 mm) trade size in buildings or for exterior above ground installations.

          - The minimum conduit size shall be 1 inch (25 mm) trade size for underground and under building slab installations.

          - ½ inch (13 mm) EMT/FMC or 3/8 inch (10 mm) FMC permitted under certain conditions addressed elsewhere in these Specifications or as detailed on the Drawings.

        - Conduit systems shall be worked into complete, integrated arrangements, with like elements to present an orderly, neat, and workmanlike appearance as specified herein.

        - Install conduit, raceways, junction boxes and device back boxes concealed, except as shown or noted otherwise.  Conduits, raceways, junction boxes and device back boxes may be exposed in unfinished areas or in mechanical equipment rooms.  Where conduits or raceways are exposed, above suspended ceilings, or under raised floors, they shall run parallel with walls or structural elements.

        - Vertical runs shall be plumb; horizontal runs level and parallel with structure, as appropriate.  Groups shall be racked together neatly with both straight runs and bends parallel and uniformly spaced.

        - Install as high as practicable to maintain adequate headroom shown or required.  Notify University before installation whenever headroom of less than 7 feet 6 inches (2.3 m) will result.  Coordinate with work of other Divisions to achieve proper headroom as specified in this Section.  In area above suspended ceilings, run conduits on wall surfaces wherever possible, instead of by hanging.

        - Conduits shall be securely fastened in place at intervals of not more than those required by the Code for the respective conduit type and size, with suitable clamps or fasteners of approved type, and vertical conduits shall be properly supported to present a mechanically rigid and secure installation.

        - Maintain at least six (6) inches (150 mm) clearance between conduit and piping.  Maintain twelve (12) inches (300 mm) clearance between conduit and heat sources such as flues, steam pipes, and heating appliances.

        - No conduit shall be fastened to other conduits or pipes or installed so as to prevent the ready removal of other pipes for repairs.  No conduits shall be attached to suspended ceiling support wiring systems or seismic bracing wiring for lighting fixtures.

        - For concrete (block or cast-in-place) structures, conduit directly supported from floor, walls, and ceiling shall be spaced out at least 1/4 inch (6 mm) using one-hole malleable straps with pipe spacers or, if three (3) or more conduits are located in a parallel run, they shall be spaced out from the structure approximately 5/8 inch (16 mm) to 1 inch (25 mm) by means of framing channel.

        - Individual conduits hung from roof structure shall be supported by split-ring hangers and wrought-iron hanger rods.  Where three (3) or more conduits are suspended from the ceiling in parallel runs, use steel channels, Kindorf, Unistrut or equal, hung from 1/2-inch rods to support the conduits.  The conduit on these channels shall be held in place with conduit clamps designed for the particular channel that is used.

        - Secure conduit racks to concrete walls and ceilings by means of cast-in-place anchors; die-cast, rustproof alloy expansion shields; or cast flush anchors.  Wooden plugs, plastic inserts, or gunpowder driven inserts shall not be used as a base to secure conduit supports.  Conduit shall be supported immediately on each side of a bend and not more than three (3) feet (0.9 m) from an enclosure where a straight run of conduit ends.

        - Welding, brazing, or other heating of the conduit is not permitted.

        - Clearance:  Do not obstruct spaces required by Code in front of electrical equipment, access doors, etc.

        - Conduits, two (2) inches (50 mm) trade size or smaller O.D. but not larger than one-third concrete thickness, may be installed in structural concrete, between steel and bottom of slab, only where permitted by the Project Manager.  Conduit may be in contact with reinforcing or other conduit where crossing at right angle, but maintaining minimum spacing of three times O.D. elsewhere.

        - The interior of raceways shall be thoroughly clean and free form cement, paint, grease, plaster, and dirt.

        - Empty conduit in which wire is to be installed by others, including telephone and computer conduits, shall have pull lines installed.  The pull line shall be 3/32 inches (2.3 mm) nylon or polyolefin having not less than 200 pound (90.7 Kg) tensile strength.  No less than twenty-four (24) inches (600 mm) of slack shall be left at each end of the pull line.  Attach a tag approved for the purpose to ends of pull line with nylon string and marked in indelible ink with location of other end and service for which conduit is provided.

        - Fire Alarm System conduits and raceways, shall have junction box covers painted red and labeled "FIRE ALARM" in white letters.

      - CONDUIT - INSTALLATION

        - Drawings indicate, generally, routes of branch circuits.  Runs to panels are indicated as starting from nearest outlet.  Provide conduits to panels as though routes were indicated in their entirety.

        - Subcontractor shall not commence installation of conduits until conduit runs have been accounted for and properly planned.

        - Conduits shall be continuous from panels to distributing centers, outlets or switches.  Pull boxes and splice boxes shall be installed where shown and where otherwise required to facilitate installation of conductors and to comply with code requirements.  Different types of conduits shall not be intermixed in run.

        - Conduits shall be installed to be free of traps, where condensation water could accumulate.

        - When required for ease of cable pulling and as necessary to meet code, provide malleable conduit fittings or pull boxes even though not shown.  Turns shall consist of malleable fittings or concentric bends.

        - Bends and offsets shall be avoided where possible, but where necessary, shall be made with an approved one shot bender or conduit-bending machine.  Make bends and offsets of as large a radius as construction will permit so as not to damage the conduit.  Conduit bends shall not be kinked and shall not be flattened more than 5 percent of the outside diameter of the conduit.  Where exposed conduits are run in groups, bends shall have a common center, with minimum inner radius eight times inside diameter of conduit.  Standard elbows are not allowed at these locations.

        - The use of ½ inch (13 mm) conduit is permitted for the following.

          - Lighting switch legs where there are not more than 6 conductors.

          - EMCS/FMCS and other Class 2 or 3 control and signal wiring.

        - The use of flexible conduit is restricted.  Flexible conduit is not permitted in walls, above inaccessible ceiling spaces or within other concealed or inaccessible spaces.  A bare equipment grounding conductor shall be installed in conduit runs having a length of flexible metallic conduit, liquid-tight flexible metal conduit, or non-metallic conduit as part of the run.  Liquid-tight flexible metal conduit shall be used in damp or wet locations requiring flexible conduit.

          - Flexible metal conduit or liquid-tight flexible metal conduit is permitted for final connection to transformers, rotating or vibrating equipment.  The length of size or type flexible conduit shall not exceed three (3) feet (900 mm) for this purpose.

          - Flexible metal conduit or liquid-tight flexible metal conduit to sensors on piping shall not exceed four (4) feet (1200mm).

          - Above suspended ceilings, flexible metal conduit, 3/8 inch trade size minimum, is permitted for final connection from the above ceiling outlet box to the light fixture.  Flexible metal conduit to light fixtures shall not exceed six (6) feet (1800 mm).

        - Plug or cap unused conduit openings with a suitable device designed for the purpose.  Caulking compound shall not be used for plugging conduit openings.  Plug conduit with approved firestop material where conduits leave heated area and enter unheated area.

        - Provide escutcheon plates at exposed wall, ceiling, and floor conduit penetrations.  Provide prime painted split escutcheons where exposed conduits enter walls, ceilings or floors in finished rooms.  Use Crane Co. No. 10 BC, Grinnel, or equal.

        - Underground stub-ups shall use wrapped or PVC-coated rigid steel galvanized 90-degree elbows with a minimum radius not less than that permitted by Code or as noted on the Drawings and wrapped or PVC-coated rigid steel galvanized conduit riser.

        - Flash and counter flash conduits through roof.

        - Penetrations (Where not cast-in place):

          - Pack space between conduit and hole in walls and floors with approved firestop materials for water and airtight seal.  Refer to Division 07, Section 078413, Penetration Firestopping, for approved materials and methods of installation

          - Make penetrations through walls and floors watertight with approved firestop materials, even though concealed within walls or furred space.

          - Make penetrations through damp proofed/water proofed surfaces by appropriate means to maintain integrity of system penetrated, including penetrations caused by hangers suspended off such surfaces.

          - After the conduit is installed, the packed opening shall be painted to match the adjacent surface.

        - Penetrations through Concrete:  Provide galvanized rigid steel nipples threaded both ends before concrete is poured.  Each end of nipples shall extend three (3) inches beyond wall or floor surfaces.

          - Provide standard pipe caps on each end of each empty nipple.

          - Where conduit of smaller size than nipple or individual cables pass through nipples, pack annular space with fire-inert material, in accordance with Division 07, Section 078413, Penetration Firestopping, for a minimum depth of two (2) inches (50 mm) each side or three (3) inches (75 mm) on one side.

          - Where grout is noted provide Dry Wall Products, Inc. "Waterplug", U.S. Grout Corp., or equal, mixed and placed in accordance with manufacturer's instructions and three (3) inches (75 mm) minimum depth.

        - Rigid Metal Conduit:  Connect with threaded ends, fully threaded couplings, thread into integrally cast hubs or use double locknuts and insulating bushings.  Threadless fittings are not acceptable.

        - Electrical Metallic Tubing:  Connect with compression type connectors and couplings.

        - Rigid steel conduit to EMT connection shall consist of EMT connector and threaded rigid conduit coupling.

        - Where rigid steel conduit is installed in concrete slab on grade provide three (3) inches (75 mm) minimum thickness concrete encasement below conduit, tape wrap conduit with two layers of half-lapped 10-mil thick, black virgin vinyl polyethylene tape or factory-applied epoxy or PVC coating.

        - Keep conduits closed and moisture-tight during construction.

        - Conduit runs across roofs shall be supported [on redwood stand-off supports not less than six (6) inches (150 mm) nor more than eight (8) inches (200 mm) above the roof surface, and at intervals not greater than eight (8) feet (2.4 m).  The supports shall be set in asphalt on tar roofs or other roofs where asphalt is a compatible agent, or shall be securely fastened to the roof with an appropriate roofing adhesive material on roofing materials where asphalt is not a compatible material.][as detailed on the Drawings.]

        - Conduit systems used for telephone/data system cabling shall not have more than a sum of 270-degree of bends between pull boxes, outlet boxes or termination closets.  Condulet fittings shall not be used in such conduit systems.

        - No conduit shall be installed exposed on floor in areas except when approved by the project design engineer or inspector.

      - UNDERGROUND CONDUIT INSTALLATION

        - Depth of conduit shall be thirty (30) inches (760 mm) minimum to top of conduit.  Where interference with other underground work occurs, conduits shall pass below the other work.

        - Grade conduits uniformly to drain to manholes.

        - Wrap direct-buried galvanized steel conduit with two layers of half-lapped 10-mil thick, black virgin vinyl polyethylene tape or factory-applied epoxy or PVC coating.  In either case, exposed threads or damage to coating or tape shall be repaired prior to backfilling.

        - Conduit systems, to be occupied by communications conductors, shall be separated from power distribution conduits by twenty-four (24) inches (600 mm) of well-tamped earth.

        - Conduit Route Marking:

          - To safeguard the conduits below, mark the route of direct-buried conduits using continuous warning tape buried in the trench above the conduits.

          - In unpaved areas, bury the tape in the trench twelve (12) inches (300 mm) below the surface.  In paved areas, install the tape in the trench just below the pavement section.

          - Take necessary precautions to ensure that the warning tape is not pulled, distorted, or otherwise misplaced during backfilling.

        - Add magnetic #10AWG tracer wire top of the underground non-metallic conduits or duct banks.  The tracer wire shall be continuous along the path of the duct banks and conduit stub ups and shall be exposed in the manholes and at each stub up with minimum of twenty-four (24) inches (600 mm) pigtail in an embedded concrete box.  Refer to Division 01, Section 013500, Special Procedures, Paragraph 3.1.C, for additional details.

        - Duct spacers shall be used to install ducts for maintaining duct spacing during concrete pour.  The spacers shall be tied together with the ducts and reinforcement bars to form one integrated assembly.

      - GROUNDING

        - Permanently and effectively ground conduit systems in accordance with Division 26, Section 260526, Secondary Grounding for Electrical Systems.  Grounding type bushing shall be grounded with the equipment ground wire.

        - A separate ground conductor shall be run in each conduit and shall be connected to each junction box using a grounding screw in each box.  An equipment bonding jumper shall be used to connect grounding type receptacles to the grounded box.  The use of looped wires under grounding screws shall not be permitted.

      - INTERFACE WITH OTHER SYSTEMS

        - Install conduit to preserve fire resistance rating of partitions and other elements, using materials and methods under the provisions of Division 07, Section 078413, Penetration Firestopping.

        - Route conduit through roof openings for piping and ductwork or through suitable roof jack with pitch pocket.

        - Refer to Division 26, Section 260500, Common Work Results for Electrical, for removal of disconnected wiring from the raceway systems and tagging requirements.

END OF SECTION 260533