SECTION 260536 – CABLE TRAYS FOR ELECTRICAL SYSTEMS

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Cable trays - Ladder, Ventilated Bottom and Solid Bottom Type.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 01, Section 013523.11, Lateral Force Provisions.

          - Division 07, Section 078413, Penetration Firestopping.

          - Division 26, Section 260500, Common Work Results for Electrical.

          - Division 26, Section 260501, Inspections and Testing for Electrical Work.

          - Division 26, Section 260519.11, 600 Volt Conductors and Cable.

          - Division 26, Section 260523, Low-Voltage Electrical Power Conductors and Cables (24 Volt AC/DC or Less).

          - Division 26, Section 260526, Secondary Grounding for Electrical Systems.

          - Division 26, Section 260533, Electrical Conduit.

          - Division 26, Section 260533.13, Boxes for Electrical Systems.

          - Division 26, Section 262726, Wiring Devices.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated.  Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01, Section 010000, General Requirements, for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - ASTM International.

        - LBNL Construction Details and Design Guidelines (CDDG), Vol. 3 – Construction Details, Part VI – Electrical Details.

        - NEMA – National Electrical Manufacturers Association.

      - SUBMITTALS

        - Submit under provisions of Division 01, Section 010000, General Requirements, “Submittals”; Division 01, Section 013500, Special Procedures, “Drawings and Specifications”; Division 26, Section 260500, Common Work Results for Electrical, “Submittals"; and as required by other sections of the Specifications.

        - Shop Drawings:  The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01, Section 010000, General Requirements, “Submittals”; and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the LBNL Facilities Division Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Submit product data for materials and equipment of the cable tray system components proposed for use.  Clearly identify the specific products and material intended to be used.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26, Section 260500, Common Work Results for Electrical.

        - Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards.  No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

        - Refer to Construction Drawings for the type of the cable trays to be furnished and installed under this project.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver materials to site in unopened cartons or bundles as appropriate, clearly identified with manufacturer's name, Underwriters’ or other approved label, grade or identifying number.

        - Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect equipment and material from dirt, water, construction debris, and traffic.

- PRODUCTS

      - MANUFACTURERS

        - Husky/Burdy

        - Globe

        - Cooper B-Line Cable Tray

      - GENERAL

        - All electrical materials shall be new and within one year of manufacture, complying with the latest codes and standards.  No used, re-built, re-sold through secondary market (salvage, recycle, etc.), refurbished and/or re-manufactured electrical materials shall be furnished and installed on this project.  Completed tray lengths and fittings shall be hot-dip galvanized after fabrication and welding.

        - All straight tray sections, angles, offset, corners, cable dropouts, reducers, splice plates, coupling connectors, covers including tray fittings and hardware shall be from the same selected manufacturer.

        - Trays shall be fabricated of No. 14 gauge (1.99 mm) minimum thickness steel.

        - Bends, both horizontal and vertical, shall have a minimum center radius of [12 inches (300 mm)] [24 inches (600 mm)], unless otherwise indicated.

        - Trays shall have an overall side rail height of [4 inches (100)] [6 inches (150 mm)] with a minimum loading depth of [3 inches (75 mm)] [5 inches (125 mm)].  Tray width shall be [6 inches (150 mm)], [12 inches (300 mm)], [18 inches (450 mm)], [24 inches (600 mm)], [30 inches (760 mm)] and [36 inches (900 mm)] in accordance with the Construction Documents.

        - Tray brackets with integral tray clamps assembled as a part of the bracket shall be provided.  The assembly shall be of such a design that one tray clamp shall be stationary and the other shall require the tightening of one bolt only, or its equivalent, in order to securely clamp and position the tray.

      - LADDER CABLE TRAYS

        - Ladder type cable trays shall consist of minimum [4 inches (100)] [6 inches (150 mm)] deep two longitudinal solid sides with cable supporting transverse members (rungs), spaced at not more than [6 inches (150 mm)] [9 inches (225 mm)] on center.

        - All transverse members shall have rounded edges that will not damage cable insulation and may be used as dropouts without further cable protection.

        - No portion of the rungs shall protrude below the bottom plane of the side rails.

      - Ventilated trough cable trays

        - Trough type cable trays shall consist of two longitudinal side rails with a corrugated or flat bottom welded to the side rails.

        - The bottom shall have rectangular holes [2-1/4 by 4 inches (63 by 100 mm) or manufacturer’s standard] punched through for ventilation in the tray.

        - The cable trough shall be burr free and smooth to avoid cable damage during installation.

      - solid trough cable trays

        - Solid bottom tray shall consist of two longitudinal members (side rails) with a solid corrugated or flat surface bottom.

        - The corrugated solid bottom shall be welded to the side rails and shall have minimum flat cable bearing surface of 2-3/4 inches (70 mm) spaced at 6 inches (150 mm) on centers.

- EXECUTION

      - INSTALLATION

        - Install cable tray in accordance with manufacturer's instructions and Construction Drawings.

        - Support cable tray system on 8-foot centers (maximum), at bends, and tee fittings in accordance with the manufacturer’s recommendation, codes and standards, and construction documents.

        - Connect sections of cable tray together with edges free from burrs and sharp projections.

        - Cable tray shall be supported on trapeze-style hangers, 1-5/8 by 1-5/8 inches (10 by 10 mm) channel and 1/2 inch (13 mm) diameter threaded-rod hangars from preset concrete inserts.  The tray supports shall be spaced in accordance with the requirements of NEC and manufacturer.  Refer to Construction Drawings for additional installation details.

        - Tray system shall be assembled as one raceway system in accordance with the Construction Drawings.  Splice plates shall be used for connecting straight sections and fittings with provision for thermal expansion.  The nuts and bolts shall be installed so as not to damage the cables during their pull in the trays.

        - Install #2/0AWG copper jumper ground wire at each tray splice, fitting and between tray systems with connection to ground grid at minimum of two places at trays’ ends.

        - Take-off conduits shall be grounded via grounding bushing and jumper to the tray grounding system.

        - Tray covers shall be installed with clamps on trays in areas exposed to accidental touch by personnel, damage due to process piping above the tray, and where shown or noted on the Construction Drawings.  The tray covers under process piping shall extend at least 18 inches (457 mm) beyond each side of the piping.

END OF SECTION 260536