SECTION 260923 – lighting control devices

- GENERAL

      - SUMMARY

        - This section applies for LEED-NC, LEED-CS, and LEED-CI Prerequisites EA 2, which require compliance with ASHRA/IESNA 90.1-2004.  ASHRA/IESNA 90.1-2004, Section 9, “Lighting,” sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:  Local switches, occupancy sensors, and daylight-harvesting controls can be used to meet the requirements of LEED-NC and LEED-CI Credits EQ 6.1.  However, the use of task lighting may also be required, depending on the type of lighting system used on the project.  Occupancy sensors and daylight-harvesting controls can be combined with other energy-conserving measures to meet the requirements of LEED-NC, LEED-CS, and LEED-CI Credits EA 1.

          - Occupancy sensors.

          - Power supply:

            - Relays.

            - Supply wiring.

          - Control wiring.

          - Control panels.

        - Related Sections:

          - Division 01, Section 010000, General Requirements.

          - Division 01, Section 013500, Special Procedures.

          - Division 13 Sections.

          - Division 26, Section 260500, Common Work Results for Electrical.

          - Division 26, Section 260501, Inspections and Testing for Electrical Work.

          - Division 26, Section 260519.11, 600 Volt Conductors and Cable.

          - Division 26, Section 260533, Electrical Conduit.

          - Division 26, Section 260533.13, Boxes for Electrical Systems.

          - Division 26, Section 262726, Wiring Devices.

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated.  Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01, Section General Requirements, for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

        - ANSI/NFPA 70 - National Electrical Code.

        - ASHRAE 85 - Automatic Control Terminology for Heating, Ventilating, Air Conditioning.

        - ASME MC85.1 - Terminology for Automatic Control.

        - LBNL Construction Details and Design Guidelines (CDDG), Vol. 3 – Construction Details, Part VI – Electrical Details.

        - LBNL Electrical Authority having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program).

        - LBNL Electrical Safety Manual.

        - LBNL Pub-3000 Chapter 8 - Electrical Safety Program.

        - LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program.

        - LBNL Pub-3000 Chapter 18 - Lockout/Tagout Program.

        - MIL-S-29175 - Switch, Thermostatic, Low Voltage, Non- (Setback/Setup) and Setback/Setup), Limiting:  Heating, Cooling and Heating-Cooling.

        - NEMA – National Electrical Manufacturers Association:

          - NEMA EMC1 	Energy Management Systems Definitions.

          - NEMA ICS 1 	Industrial Control and Systems: General Requirements.

          - NEMA ICS 2 	Industrial Control and Systems: Controllers, Contactors, and Overload Relays Rated 600 Volts.

          - NEMA ICS 6 	Industrial Control and Systems: Enclosures.

          - NEMA ST 1 	Specialty Transformers (Except General Purpose Type).

        - NETA ATS - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems.

        - UL – Underwriters' Laboratories:

          - UL 485 	Motor Control Centers.

          - UL 489 	Molded Case Circuit Breakers and Enclosures.

          - UL 508 	Industrial Control Equipment.

      - DEFINITIONS

        - EMCS - Energy Monitoring Control System.

        - DDC - Direct Digital Controller/Direct Digital Control.

        - BAS - Building Automation System.

      - SYSTEM DESCRIPTION

        - The purpose of the project is control the "on/off" operation of specific lighting and space conditioning systems.  The means of accomplishing this is through the installation of individual room lighting "occupancy sensors" to control the operation of the lighting and space conditioning systems.

      - SUBMITTALS

        - Submit under provisions of Division 01, Section 010000, General Requirements, “Submittals”; Division 01, Section 013500, Special Procedures, “Drawings and Specifications”; Division 26, Section 260500, Common Work Results for Electrical, “Submittal" ;and as required by other sections of the Specifications.

        - Shop Drawings:  The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01, Section 010000, General Requirements, “Submittals”, and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the LBNL Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Shop Drawings and Product Data:

          - Submit Shop Drawings to NEMA ICS 1 indicating location of occupancy sensor system components, wiring connections and diagrams, dimensions.

        - Manufacturer's Installation Instructions:  Include for manufactured components.

        - Submittal of automatic control systems components which are not the product of the control system manufacturer shall bear evidence of its approval.

        - Submit field reports indicating operating conditions after detailed check out of systems at Date of Substantial Completion.

        - Project Record Documents:

          - Accurately record actual locations of control components, including relays, power supplies, and sensors.

          - Revise Shop Drawings to reflect actual installation and operating sequences.

          - Include data specified in "Submittals" in final "Record Documents" form, according to Division 01, Sections 010000, General Requirements; and Section 013500, Special Procedures.

          - Provide as-built equipment location and wire routing diagrams, as-built termination and interconnection drawings as well as as-built elementary diagrams.

          - Provide detailed set-up information for furnished equipment, indicating required initial configuration switch settings, jumper positions, to facilitate equipment replacement.

        - Operation and Maintenance Data:

          - Include interconnection wiring diagrams complete field installed system with identified and numbered, system components and devices.

          - Include operation and maintenance manuals for equipment and devices, including sensors, power supplies, and other equipment furnished.

          - Include recommended preventive maintenance procedures and materials.

          - Include systems descriptions, set points, and controls settings and adjustment.

          - Include inspection period, cleaning methods, cleaning materials recommended, and calibration tolerances.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26, Section 260500, Common Work Results for Electrical.

        - Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards.  No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

        - Manufacturer's Qualifications:  Company experienced in manufacturing the products specified in this Section with minimum five (5) [ten (10)] years documented experience.

        - Installer Qualifications:  Company experienced in applying the work of this Section with minimum five (5) [ten (10)] years documented experience approved by manufacturer.

          - The installer shall furnish labor and materials, install the necessary hardware, accomplish the necessary wiring, interfacing and panelwork, and place into operation the system as specifically stated in the specifications and drawings.

          - The installer shall have a complete [engineering,] installation and service operation within the area.

        - The electrical standards shall comply with NEMA standards pertaining to components and devices for electric-electronic Energy Management Control Systems (EMCS).

        - Substitutions:  Where Subcontractor proposes substitutions to specified equipment, Subcontractor shall provide necessary technical documentation, and if required, samples and/or demonstrations, to enable the University to evaluate the proposed equipment.

      - DELIVERY, STORAGE AND HANDLING

        - Care shall be taken to prevent damage to materials and equipment during transporting, loading, and unloading.  Packaged units shall be delivered in their original unopened crates, cartons, or boxes.  Equipment and materials shall be stored indoors in a clean, dry space.

      - COORDINATION

        - Refer to Division 01, Section 010000, General Requirements, “Coordination of Work”; and Division 26, Section 260500, Common Work Results for Electrical.

        - Refer to Division 01, Section 013500, Special Procedures, “Coordination”; and Section 013500A, Supplement for Equipment Energization Plan: Energization Validation & Authorization Package (EVAP).

        - Refer to the LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

        - Ensure installation of components is complementary to installation of similar components in other systems.

        - Coordinate installation of system components with mechanical systems equipment such as air handling units and air terminal units.

        - Ensure system is completed and commissioned by Final Acceptance.

        - Disruptions in system operation shall be specifically scheduled in advance with the University, and shall occur at exactly the scheduled time and for not greater than the scheduled duration.  Permission for unscheduled interruptions shall be specifically requested on an individual basis.

        - Under no circumstances shall operation of a system be interrupted without prior notification and approval by the University.

      - WARRANTY

        - Warranty period of one (1) year minimum shall start at the date the equipment is energized after acceptance by the University.

      - MAINTENANCE SERVICE

        - Free maintenance services shall be provided by the control system supplier for 1 year after final system acceptance in accordance with Division 26, Section 260500, Common Work Results for Electrical.  These services shall consist of manufacturer's factory-trained representatives providing emergency repair service with on-site response within 24 hours of call, all test equipment and hardware necessary for maintenance and repair work and installation of hardware modifications designed to improve system performance or eliminate known problems or deficiencies.

        - Submit written reports on each inspection or maintenance service to LBNL.

      - EXTRA MATERIALS

        - Provide as spare parts two (2) of each type and model of sensor, power pack, slave relay.

        - Provide spare parts under provisions of Division 01, Sections 010000, General Requirements; and Section 013500, Special Provisions.

- PRODUCTS

      - MANUFACTURERS

        - Watt Watcher - Model [__________.],Light-O-Matic - Model [__________.], or equal.

        - Substitutions:  Under provisions of Paragraph 1.6.F of this Section and Division 01, Section 010000, General Requirements.

      - POWER SUPPLY

        - External power supply shall be 120 [277] VAC, 60 HZ, with the following characteristics:

          - Secondary output 24Vc, 100mA minimum.

          - Transformer and contact closure relay in single unit.

      - RELAYS

        - Contacts:  NEMA ICS 2; Form [A.] [C.].

        - Contact Ratings:  NEMA ICS 2; Class [A150.].

        - Auxiliary Relays:  Provide sufficient SPDT auxiliary relay contacts [for each detection zone] to provide accessory functions specified.

      - OCCUPANCY/MOTION SENSORS

        - If both infrared and ultrasonic sensors are utilized, they shall be of like manufacturer, with interchangeable heads, so that an utltrasonic head may be substituted for an infrared head and vice versa, without necessity for replacement of other devices (i.e., Slave relays, power supplies, et al.), and shall be interchangeable in mounting, utilizing the same size cutouts, connectors, etc.

        - Sensing system shall incorporate a time-delay-before-off relay, adjustable from 5 to 20 minutes.

        - Occupancy sensors shall include a manual override to energize the lighting system upon failure of the occupancy sensor, or occupancy sensor design/installation shall provide for the lighting system to automatically remain in operation upon a failure of the occupancy sensor.

        - Outdoor motion sensors shall be rated and labeled for outdoor conditions and operations and impervious to the effects of ultraviolet rays.

- EXECUTION

      - EXAMINATION

        - Verify that systems are ready to receive work.

        - Beginning of installation means installer accepts existing conditions.

      - INSTALLATION

        - Install system in accordance with manufacturer's instructions initially set for a 10 minute delay.

        - Occupancy Sensors:

          - Occupancy sensors will be furnished for each of the rooms specified in the input/output points list, or as proposed and approved by the University.  Occupancy sensors shall be provided for each room to provide 100 percent coverage of the room.  In large areas requiring multiple sensors, occupancy sensors shall be installed in sufficient numbers and in such locations as to provide overlap between zones of coverage of individual sensors, thereby insuring positive indication of occupancy in portions of each lighting area.

          - Occupancy sensors shall be ceiling-mounted, and shall incorporate selective aperture attenuation and adjustments as required to prevent spurious lighting initiations, e.g., due to passing personnel in adjacent area, such as corridors; HVAC operated.

          - Connect the occupancy detector output control relay(s) to [the building automation system (BAS)] [field processing unit (FPU)], [the space conditioning system], [as well as to] the local area lighting circuits, so that the occupancy detectors will turn off area lighting [and [reset the ]space conditioning system][ set points] during unoccupied periods.[  Where multiple rooms comprise a single HVAC zone (see Input/Output Points List), connect occupancy sensors in parallel, so that sensor may indicate the zone is occupied.

          - Slave relays or other components related to the occupancy detectors shall be mounted in proximity to the occupancy sensors,[ in NEMA 1 enclosures,] and locations shall be indicated on Shop Drawings to be approved by the University, and on "as-built" documentation furnished by Subcontractor.

          - In addition, Subcontractor shall identify locations of relays or other devices above ceilings by a standardized method of conspicuous visual indication on the ceiling at the time of installation of such devices by Subcontractor, the method of indication to be directed by the University.

          - Under no circumstances shall emergency or egress lighting be controlled by the occupancy-sensing controls.

          - One or more relay contacts shall be wired to control the lighting in such a way that the local light switch can turn off the lights, but when the switch is turned on, the occupancy detector contact can still turn the lights off.

        - Field Wiring:

          - Subcontractor shall furnish and install necessary wire, conduit, tubing, pull boxes, connection boxes, fittings, , and other materials as required to provide an automatic lighting control  system in accordance with [the Specifications and Drawings and] the equipment suppliers' specific and general installation instructions and recommendations.

          - For purposes of fire safety and wiring integrity.  The wire/cable specification calls for the installation of "plenum" rated cable.

          - Refer to Division 25, Section 255000, Facilities Monitoring and Control System.

        - Location:

          - Sensor installations shall be subject to the University's approval as to location, mounting, insertion length, and wiring.

      - SEQUENCE OF OPERATIONS

        - Occupancy sensors shall initiate lighting operation in an area upon entry of one or more persons, and shall maintain uninterrupted lighting operation throughout the period that the area is occupied.  In open areas, or areas with less than full height partitions, occupancy of portion of the area shall initiate operation of the lighting throughout the area, except where the University specifically directs otherwise.

        - When an area is vacated the lighting shall remain in operation for the adjustable time delay period.

        - The occupancy sensor coverage and sensitivity shall be adjusted so that an occupant in portion of a controlled room moving a hand in plane at approximately one (1) foot per second will trigger at least one occupancy sensor.

      - FIELD SERVICES AND TEST

        - Tests shall be made in the presence of an LBNL Inspector or the Electrical AHJ’s designated representative.  The application or interruption of power shall be programmed and directed in accordance with the approved EVAP, inclusive of the Equipment Energization Plan and necessary permits, work tasks, and safety compliance steps.

        - It shall be the Subcontractor's responsibility to ensure the proper operation of the lighting control system.

        - Start-up commission systems.  Allow sufficient time for start-up and commissioning prior to placing control systems in permanent operations.

        - Assist in a comprehensive acceptance inspection and test of installation details and system operational validity, including but not limited to; inspection and verification of input/out sensor locations, control device location and connection, input/output point terminations, point-by-point proof of function for each occupancy sensor and input/output device.

        - An unsatisfactory condition revealed by these test results, or unsatisfactory methods of tests and/or testing apparatus and instruments, shall be bought to the attention of the Project Manager, Responsible Design Professional (RDP), and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.  Corrections by the Subcontractor shall be validated by re-tests to the satisfaction of the Project Manager, the RDP, and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.

      - DEMONSTRATION and acceptance

        - Demonstrate a complete and operating system to the Project Manager or his representative.

        - Final acceptance shall depend upon the satisfactory test results and performance of the system as performed in accordance with the manufacturer’s instructions.  After tests have been reviewed and approved by the University, the system may be put in to service in accordance with the approved Equipment Energization Plan and the Energization Validation and Authorization Package (EVAP).

END OF SECTION 260923