SECTION 262726 – WIRING DEVICES

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Wall switches.

          - Receptacles.

          - Floor-mounted service fittings.

          - Wall dimmers.

          - Device plates and box covers.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 26 Section "Common Work Results for Electrical".

          - Division 26 Section “Inspections and Testing of Electrical Work”.

          - Division 26 Section "600 Volt Conductors and Cable".

          - Division 26 Section "Secondary Grounding for Electrical Systems".

          - Division 26 Section "Electrical Conduit".

          - Division 26 Section "Boxes for Electrical Systems".

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, , the edition of the referenced code or standard that is current at the time of the “date of record” for the Work shall be considered the effective code or standard for the duration of the project.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to specific Division 26 Sections for additional referenced codes and standards.

        - ANSI/NFPA 70 - National Electrical Code.

        - FS – Federal Specifications:

          - FS WC-596	Electrical Power Connector, Plug, Receptacle, and Cable Outlet

          - FS W-S-896-E	Switch, Toggle

        - LBNL Construction Details and Design Guidelines; Vol. 3 Construction Details; Part VI Electrical Details.

        - LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program)

        - LBNL Electrical Safety Manual

        - LBNL Pub-3000 Chapter 8 – Electrical Safety Program

        - LBNL Pub-3000 Chapter 14 – Electrical Equipment Safety Program

        - LBNL Pub-3000 Chapter 18 – Lockout/Tagout Program

        - NEMA – National Electrical Manufacturers Association:

          - NEMA WD 1	General Color Requirements for Wiring Devices.

          - NEMA OS 3	Selection and Installation Guidelines for Electrical Outlet Boxes.

          - NEMA WD 6	Wiring Devices-Dimensional Requirements.

          - NEMA FB 11	Plugs, Receptacles and Connectors of the Pin and Sleeve Type for Hazardous Locations.

        - NETA ATS - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems

        - UL – Underwriters' Laboratories:

      - SUBMITTALS

        - Submit under provisions of Division 01 Section "General Requirements" Paragraph 1.8.F, Submittals, and Division 01 Section "Special Procedures" Paragraph 1.7, Drawings and Specifications, Division 26 Section "Common Work Results for Electrical - Submittals" and as required by other sections of the Specifications."

        - Shop Drawings: The Subcontractor shall submit for approval Shop Drawings prepared in accordance with Division 01 Section "General Requirements", Paragraph 1.8.F and as required by other sections of the Specifications.

        - All submittals and shop drawings shall be reviewed and approved by the Facilities Division Utility Group Electrical Engineer before procurement or fabrication of material and equipment.

        - Submit Shop Drawings and Product Data clearly identifying the specific product and material intended to be used.

      - QUALITY ASSURANCE

        - Products shall be tested, approved and labeled/listed by Underwriters Laboratories, Inc., or by a nationally recognized testing laboratory (NRTL) as listed in Division 26 Specification "Common Work Results for Electrical."

        - Electrical equipment and materials shall be new and within one year of manufacture, complying with the latest codes and standards. No used, re-built, refurbished and/or re-manufactured electrical equipment and materials shall be furnished on this project.

      - COORDINATION

        - Refer to Division 01 Section "General Requirements" Paragraph 1.7.

        - Refer to Division 01 Section “Special Procedures” Paragraph 1.6 and Supplement for Equipment Energization Plan and Energization Validation and Authorization Package.

        - Refer to the LBNL Electrical Authority Having Jurisdiction: Standard Procedure for Safe Electrical Installations (IAHJ Program) in regards to the Facilities Energization Validation and Authorization Package (EVAP) process necessary before equipment energization.

        - Refer to construction drawings for the type of the wiring devices to be installed and wired under this project.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver materials to site in unopened cartons or bundles as appropriate, clearly identified with manufacturer's name, Underwriter's or other approved label, grade or identifying number.

        - Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris, and traffic.

- PRODUCTS

      - WALL SWITCHES

<Revise for project requirements>

        - Wall Switches for Lighting Circuits: Industrial grade, AC switch with toggle handle, rated 20 A and 120-277 VAC. Handle: ‘White’ in non-laboratory areas, and ‘Gray’ in laboratory and hi-bay areas with stainless steel covers. Bryant No.: Single pole 4901-W (white) and 4901-GRY (gray); 3-Way 4903-W (white) and 4903-GRY (gray); and 4-Way 4904-W (white) and 4904-GRY (gray); Hubbell or equal.

        - Locator Type: Lighted handle. Bryant No.: 4901-PLC120 (clear pilot handle for 120Vac) and 4901-PLC277 (clear pilot handle for 277Vac).

      - RECEPTACLES

<Revise for project requirements>

        - In general, receptacle face color shall be white or gray (use in laboratories with stainless steel cover plate, when specified). For receptacles served from isolated ground system, the color shall be orange, receptacles served from the emergency power, the color shall be red and the surge protected receptacles color shall be blue. Refer to sections below under Paragraph for other specified colors.

        - Industrial grade, 20A, 125V, 2-pole, 3-wire, NEMA 5-20R duplex for multi-outlet 20A branch circuits or where only one receptacle is connected to a 20A branch circuit. Bryant No. 5362-W (white), 5362-GRY (gray), 5362-Red (emergency) and 5362-IG (orange); Hubbell or equal.

        - Heavy duty, 20A, 125V, 2-pole, 3-wire, NEMA 5-20R single quadplex for a 20A branch circuits, only where specified or shown on the drawings. Bryant No. 21254-W (white); Hubbell or equal.

        - Industrial grade, 30A, 125V, 2-pole, 3-wire, NEMA 5-30R single receptacle is connected to a 30A branch circuit. Bryant No. 9530-FR (black), and 9530-IG (orange); Hubbell or equal.

        - Industrial grade, 20A, 250V, 2-pole, 3-wire, NEMA 6-20R single receptacles for single 20A branch circuit. Bryant No. 5461-W (white), 5461 (gray), and 5461-Red (emergency); Hubbell or equal.

        - Industrial grade, 20A, 250V, 2-pole, 3-wire, NEMA 6-20R duplex receptacles for a 20A branch circuit. Bryant No. 5462-W (white), 5462-GRY (gray) and 5462-Red (emergency) and 5462-IG (orange); Hubbell or equal.

        - Industrial grade/Heavy duty, 30A, 250V, 2-pole, 3-wire, NEMA 6-30R single receptacle for a 30A branch circuit. Bryant No. 9630-FR (black) and 9630-IG (orange); Hubbell or equal.

        - Industrial grade/Heavy duty, 20A, 250V, 3-pole, 4-wire, NEMA 15-20R single receptacle for a 20A branch circuit. Hubbell No. HBL8420 (black) or equal.

        - Industrial grade/Heavy duty, 30A, 250V, 3-pole, 4-wire, NEMA 15-30R single receptacle for a 30A branch circuit. Bryant No. 8430 (black); Hubbell or equal.

        - Industrial grade/Heavy duty, 50A, 250V, 3-pole, 4-wire, NEMA 15-50R single receptacle for a 50A branch circuit. Bryant No. 8450-FR (black); Hubbell or equal.

        - Industrial grade/Heavy duty, 60A, 250V, 3-pole, 4-wire, NEMA 15-60R single receptacle for a 60A branch circuit. Bryant No. 8460-FR (black); Hubbell or equal.

        - Twist lock, industrial grade, 20A, 120/208V, 4-pole, 5-wire, NEMA L21-20R single receptacle for a 20A branch circuit. Hubbell No. HBL2510 (black) and IG2510 (orange) or equal.

        - Twist lock, industrial grade, 20A, 277/480V, 4-pole, 5-wire, NEMA L22-20R single receptacle for a 20A branch circuit. Hubbell No. HBL2520 (black) or equal.

        - Ground Fault Interrupting, duplex receptacle, 20A, 125V, 2-pole, 3-wire, NEMA 5-20R. Bryant No. GFR53FT-W (white), GFR53FT-GRY (gray); Hubbell or equal.

        - All other special purpose receptacles/plug assemblies as specified on the construction drawings.

      - FLOOR-MOUNTED SERVICE FITTINGS

<Revise for project requirements>

        - Flush Covers for Duplex Convenience Receptacle:  [Brass] [Aluminum] flush cover suitable for floor box, with [duplex-flap] [duplex-threaded] opening.  [Provide [brass] [aluminum]-finish protective rings for use with threaded openings] [Provide brass carpet rings.]

        - Flush Covers for Communications:  [Brass] [Aluminum] flush cover suitable for floor box, with 2-1/8 x 1-inch combination threaded opening.  [Provide [brass] [aluminum] finish [protective rings] [split nozzle.] [Provide brass carpet rings.]

        - Poke-Through Fittings: Listed by NRTL as fire-rated poke-through device; include fire stops and smoke barriers in through-floor component.  Terminate in 4-inch square by 2-1/2 inch (62 mm) deep junction box.

      - WALL DIMMERS

<Revise for project requirements>

        - Wall Dimmers:  NEMA WD 2; [rotary-dial] [linear-slide] type.

        - Rating:  600 W minimum, larger size to accommodate load shown on drawings.

      - DEVICE PLATES and box covers

<Revise for project requirements>

        - In non-laboratory finished areas, the cover plates for flush mounted devices shall be impact resistant white plastic type, and in laboratories and hi-bay areas, these shall be Type 302/304 stainless steel. Device plate manufacturer shall be the same as other flush mounted device plates. Use jumbo size plates for devices installed in masonry walls.

        - Weatherproof Cover Plate: Metal, hinged device cover with provision for cord attachment with cover closed.  TYMAC #MM400 or approved equal.

        - Device Plates on Surface Outlets: shall match the type of the box device is mounted on. Provide matching gasketed cover plates for devices mounted in FS and FD boxes. Type Crouse-Hinds (WLRS-1, -2, WLRD-1, WLGF-FS, DS224, DS21G, DS35, DS/DSS23, DS32, DS185 etc.), Appleton or equal.

- EXECUTION

      - INSTALLATION

        - Install devices and wall plates flush and level.  Plates shall be plumb and with edges in continuous contact with adjacent finished surfaces.

        - Install wall switches [48 inches (1200 mm)] [     ] inches above floor, OFF position down.

        - Install wall dimmers [48 inches (1200 mm)] [     ] inches above floor; de-rate ganged dimmers as instructed by manufacturer. Do not use common neutral.

        - Unless noted otherwise on the Drawings, install convenience receptacles 15 inches (380 mm), on center, above floor or finished grade, [12 inches (300 mm)] [____] inches above [counters,] [backsplash,] with grounding receptacle pole on top.

        - Install specific-use receptacles at heights, shown on construction drawings.

        - Mounting positions for receptacles with ground or neutral pins, 15 to 60 amps, non-locking and locking:

          - Receptacles vertically mounted at 48 inches or less above the finished floor shall be positioned with the ground pin on top.

          - Receptacles vertically mounted above 48 inches above the finished floor shall be positioned with the ground pin at the bottom.

          - Vertically mounted GFCI receptacles at any height shall be positioned with the ground pin on the bottom.

          - Receptacles with a neutral pin and horizontally mounted at any height shall be positioned with the neutral pin on top.

        - Drill opening for poke-through fitting installation in accordance with manufacturer's instructions.

        - Provide weatherproof, gasketed cover plates on flush mounted devices where shown, type and configuration to suit flush device and its orientation.

        - Install blank and device cover plates on switches, receptacles and boxes.

        - Provide GFCI protected 20Ampere receptacles in accordance with NEC - "Ground Fault Protection for Personnel" in bathrooms, garages, and receptacles mounted outside, and within 6 feet (1.8 m) of sinks in kitchen areas.

        - All GFCI receptacles in wet and damp areas shall be in weatherproof enclosure.

        - In addition, GFI protection shall be provided for:

          - Electrical receptacles within 6 feet (1.8 m) of the sinks or developing tanks in Dark rooms, and within 6 feet (1.8 m) of chemical bath tanks in electrolysis areas.

          - Laboratory receptacles within 6 feet (1.8 m) of the sink, including sinks inside fume hood enclosures.

          - Out-door electrical receptacles with weatherproof enclosure/protection.

          - Receptacles within six feet of an emergency eye wash/shower station.

          - Receptacle feeding water cooler units and drinking fountains.

      - GROUNDING

        - Permanently and effectively ground wiring devices in accordance with Division 26 Section "Secondary Grounding for Electrical Systems".

      - field quality control

        - Once receptacle branch circuits have been tested and energized in accordance with the approved Equipment Energization Plan and Energization Validation and Authorization Package perform the following tests on receptacles.  Tests shall be made in the presence of an LBNL Inspector or the Electrical AHJ’s designated representative.

        - An unsatisfactory condition revealed by these test results, or unsatisfactory methods of tests and/or testing apparatus and instruments, shall be bought to the attention of the Project Manager, Responsible Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.  Corrections by the Subcontractor shall be validated by re-tests to the satisfaction of the Project Manager, the Registered Design Professional and the Facilities Division Utilities Group Electrical Engineer and/or the AHJ designated representative.

        - The Project Manager reserves the right to require that the Subcontractor perform and repeat tests that are deemed necessary to complete or check the tests of the Subcontractor at any time during the course of the work.

        - 120 volt convenience receptacles (NEMA-5-20R): For each branch circuit feeding 120-volt convenience receptacles twenty-five (25) percent of the connected receptacles shall be tested for proper voltage, polarity and grounding.

        - Ground Fault Interrupting duplex receptacles shall be tested for proper tripping and resetting operation and for proper voltage, polarity and grounding.

        - Each receptacle, other than 120-volt convenience receptacles (NEMA5-20R), shall be tested for proper voltage, polarity, and grounding.  Three-phase receptacles shall also be tested for proper phase rotation.

END OF SECTION 262726